48

SECTION 2 - GENERAL PROVISIONS
CONTENTS

1.
Introduction - Project Outline
2-2

2.
Phase Description
2-10

2.1
Phase 1
2-10

2.2
Phase 2
2-11

2.3
Phase 3
2-13

2.4
Phase 4
2-22
3.
Project Management – Guidelines
2-31
4.
SOW Terms
2-34
5.
Contractor Quality Control System (CQCS)
2-42
6.
Acceptance Tests and Documents
2-45
7.
Operation, Service and Maintenance
2-51
8.
Design Guidelines and Data
2-64
Appendix A - Guidelines for Technical Proposal
2-72
Appendix B - Guidelines for Price Proposal
2-77

1. Introduction - Project outline
1.1 General 

1.1.1 This document specifies the minimum requirements for a proposal for a turn key project (TKP) for the upgrading of Customs operational inspection site near Ashdod Port. The project includes the design, construction, installation, training, service and maintenance of the new high-energy Radiographic Inspection Facility, various additional subsystems, equipment and assemblies, furniture, as well as supplementary infrastructures and development works required for best adaptation of the new systems to the new operational procedures, according to the applicable requirements and as specified hereinafter. 

1.1.2 The guidelines specified in the SOW, drawings, lists of equipment items, etc., form only the minimum requirement, as stated above. The Contractor should take into consideration that he should design, coordinate, deliver and implement the complex which is composed of buildings, their facilities, equipment, furniture, development, etc., so as to allow full functioning of the systems as required in this SOW.

1.1.3 The Contractor shall prepare a general layout of the proposed new inspection system, taking into account the existing locations of main infrastructure, facilities and construction elements in order to enable an overall view of the deployed system in the site.

1.1.4 The Contractor shall provide a design, assuring installations and harmonious integration of the future new elements into the existing facilities and overall plan of the site and its facilities taking into account the existing facilities and operational procedures.

1.1.5 The Contractor should consider the functional and operational design requirements, without deviation from the dimensions allocated to the site area and to the existing facilities, particularly the dimensions of building D that must host the radiography system.
1.1.6 The Contractor has only some flexibility in planning, subject to the functionality of each position, its equipment and systems as specified.
1.1.7 The final planning and implementation will be carried out within a firm fixed price quotation, which will include the detailed planning and implementation the required works, sites and their contents, as specified above, as well as connecting the various buildings/positions to the utility systems (such as water, sewage, electricity, communication, etc.), including planning and implementation of additional necessary earthworks, development work, etc.

1.1.8 The Contractor undertakes to provide supply of spare parts, maintenance services and repairs for 10 years from the end of the warranty period. (See details in Clause 7.5)

With his proposal the contractor shall submit a committing price for the following services:

· Full facility comprehensive maintenance and repair services, including on site technician for all systems and subsystems (for the standard two shift and the specified options)
The price submitted should be for each year up to a period of 10 years from the end of the warranty period, with contractors' obligation for renewal the contract for each year up to the ten (10) years, according to customer wish (as defined in Clause 7.5)
1.2 Project Outline


The project, comprised of installation of the new systems as well as the intermediate system, will be implemented in four main phases. 
1.2.1 Phase 1 - Proposals Filtering


The technical and management proposals submitted by the companies in response to this tender will be evaluated, and those fulfilling all of the minimal requirements will be selected for the next phase.

1.2.2 Phase 2 - Proposal Evaluation and Performance Verification

This phase consists of two parts: tender Evaluation and system Verification 

a. Proposal Evaluation


Each proposal will be evaluated by the Evaluating Committee (EC) and scores given according to the technical evaluation table.

b. Verification tests

The objective of system verification tests is to verify the proposed system’s performance compliance with Contractor’s declarations. The tests will be conducted for the leading company; the one that achieved the best score in the evaluation phase.

These verification tests will be conducted on Contractor’s premises, with the Contractor’s staff operating the system, and obtaining the best possible screening images. 
After successful completion of the verification tests contract negotiation will start. 

Failure to comply with Contractor’s declarations will result in the system’s disqualification; therefore disengaging the Client from all obligations towards this Contractor and moving on to the succession Contractor (second best score). 

1.2.3 Phase 3 - Systems Manufacturing
This phase comprises of the following parts:

a. New Radiography system Design Reviews (PDR, DDR/CDR) Client's approval of Contractor’s design.

b. Intermediate Radiography system Design Reviews (PDR, DDR/CDR) Client's approval of Contractor’s design.

c. Site adaptations (buildings, roads, parking lots, etc.) Design Reviews (PDR, DDR/CDR) - Client's approval of Contractor’s design.

d. Safety, Security and Traffic Control systems Design Reviews (PDR, DDR/CDR) - Client's approval of Contractor’s Final design.

e. Systems manufacturing.
1.2.4 Phase 4 - Implementation
This phase comprises of the following parts:

1) Installation of Intermediate screening system 

Installation of the Intermediate screening system in Ashdod site comprises of conducting training sessions for Customer's staff, obtaining all operations' permits, etc:
· The Contractor will obtain all the necessary permits for operational service of the system from all relevant Israeli authorities prior the system acceptance tests.
· Acceptance tests - On completion of the installation of the screening system and auxiliary equipment (controls, fence, safety apparel, etc.) acceptance tests will be conducted by the Customer.
· Training sessions - Contractor responsibility.
2) Site civil works 

Dismantling works and Implementation of the changes / adaptation's works on the site 
3) New systems installations

The Contractor will obtain all the necessary permits for operational service of the systems from all relevant Israeli authorities prior the acceptance tests.
4) Preliminary Acceptance tests 

On completion of the installation of the equipment the tests will be conducted by the Contractor for each of the systems (Radiography, Control, Traffic Control, Security, etc.)
5) Trial (test) Run

The facility will be run for one month by and under the responsibility of the Contractor. During that period the customer's staff will undergo the training courses.

6) Training sessions 

After successfully passing the Preliminary Acceptance Tests (performed by the contractor) training sessions for systems operators, image analyzers, first level maintenance, instructors will be conducted. The training will be conducted in Israel. 
7) Dismantling the Intermediate system

8) Pilot  
The site will be run, for three additional months, by the customer's employees, under the supervision of the Contractor
9) Final Acceptance Tests 

At the end of that Pilot period a Final Acceptance Tests conducted by the Client, will take place. On the successful completion of these tests a warranty period of one year will commence. 

10)  Warranty Period - for 1 year.
11) Service and Maintenance - for period of 10 years.
All tasks, including tests: periodical and routine, preventive maintenance as well as routine service and maintenance of site's systems are solely Contractor’s responsibility and will be executed in Israel by the Contractor's staff only, including the on site technician. These tasks include all works required: main and peripheral systems repairs and maintenance for all systems and duration.
1.3 Description of the work 

1.3.1 General scope of the work

1.3.1.1 This statement of work (SOW) relates to the planning and implementation of a TKP designated to upgrade Customs operating site. This upgrade includes installing of a new radiographic (x-ray) inspection facility, performing the required adaptations /changes in the buildings/ systems/ Facilities/radiography tunnel / site gates/ development work, etc., as specified in this document. 

1.3.1.2 It should be noted, that during upgrading process the site will be operational and it is Contractor's responsibility to provide that all ongoing routine activities, including truck inspections shall be possible.

1.3.2 The nature of the work

1.3.2.1 The Contractor’s work includes:

Detailed planning, planning coordination, production, supply, implementation of the radiographic inspection system, buildings/structures with their contents, the infrastructures, control, safety and security systems, facilities and all the equipment, according to guidelines, planning, directing drawings, and the other specifications as defined in to this document.

1.3.2.2 The upgrading / adaptations of the site complex include, but are not limited to:

Preparation and dismantling works, existing equipment removing and debris disposal, as required by local authorities, digging and sub grading, floors, buildings, including finishing work as specified, walls, partitions, opening (doors and gates, windows, etc.), sanitary piping systems, electricity, air-conditioning, material handling systems, fire detection and extinguishing systems, equipment, furniture and underground storage items, connection of electromechanical systems to existing networks. 
The work may also include required site development works, roads, gardening, and signs, as specified in this SOW.

1.3.2.3 Acquiring all licenses required by the various Authorities, for example: Radiation safety from GOI Department of Labor, building permit, etc. is solely Contractor's task and responsibility.
1.3.2.4 All the requirements of the specifications are minimal and should serve only as guidelines for the Contractor concerning the form, nature, content and functioning of the buildings/systems/facilities/ development work, etc., which are ordered within this SOW complete, with all their parts, ready for operation, at a firm fixed price to be submitted by the Contractor in the proposal.

1.3.2.5 Project products (building/system/facility) must meet all the requirements specified in the specifications, drawings, bills of material, jointly and separately, where the documents complement each other.

The product must meet all of Contractor’s declaration as presented in his proposal.

1.3.2.6 It is emphasized that Client orders within this SOW include all works required for installation of the intermediate system and the new system, complete, finished and ready for operation, even if these are not specifically defined. 
1.3.3 Description of project works

1.3.3.1 Changes in Buildings, sites and positions

The Contractor shall carry out the changes / adaptation's works as required for the upgraded site and the new facility systems, including works and contents in the following areas (details in section  4 of this document):

a. Perimeter fencing.

b. Roads and sidewalks (site external entrance, inside the site) 
c. Parking Lots (pre-inspection, pre-clearance, adjacent to manual site)

d. Site Gates, Check-in/out cabins, work-stations.
e. Inside the Radiographic installation building (including rooms for control, operation, security checks, service, maintenance and offices).

f. Offices in the Manual Inspection site (designated for trucks to be inspected manually).

1.3.3.2 General work on the site

1.3.3.2.1 Works in the site comprise of two parts:
a. Main project: 

Works required for the technological upgrade of the site (installations of the new replaced systems).

b. Intermediate

Works required sustaining the ongoing operation of the facility during the upgrade process. (Installation of the Intermediate system including radiation shielding and auxiliary equipment required for system operation as well as temporal site adaptation as required for the operational procedures).
1.3.3.2.2 Project works comprise of installations of the following systems:

a. Radiography (X-Ray) screening systems: installing the new main system and the Intermediate system, designated to provide examination means during upgrading process. 

b. Radiography screening system testing means (devices)

c. New Conveyor system and Controls.

d.  Radiation-shielding doors, including an option to upgrade the existing doors (new radiography system).

e. Operation and Control systems (for the New and the Intermediate x-ray systems).

f. Security and safety systems (New and Intermediate systems).

g. Traffic control and monitoring systems.

h. Air-conditioning systems.

i.  Electrical, UPS and Power systems.

j. Communication systems.

k. Furniture and equipment.

l. Signposts, PA systems and Traffic lights.

m. Earthworks and development work.

n.  Buildings/Cabins.

o. Sanitation systems.

p. Gardening and irrigation work.

q.  Additional electro-mechanical systems.

r. Additional miscellaneous auxiliary sites, as required according to Contractor's proposal.

2. Phases Description
2.1 Phase 1 - Proposals Filtering

Tasks comprising project phase 1 are specified including the corresponding responsibilities as follows:

2.1.1 SOW Publishing - Client’s responsibility

The first phase of the project starts with the publishing of this SOW.
2.1.2 Contractors Site Visit - Client’s and Customer’s responsibility
Contractor's site visit will התאריך בפרסום 
Minutes of the visit, including clarifications regarding the tender will be published 1 week after the visit.
2.1.3 Proposals Submission - Bidder’s responsibility 
As a response to the Tender, the Contractor will submit its proposal for a system (or systems) to be evaluated, according the requirements of this SOW:
a. The proposal must include all the information requested in the following sections of this document and in Appendix A:

· Contractor’s company profile.
· Contractor compliance with mandatory requirements.
· Systems description, including previous deployment/upgrading experience (where operating and for how long).
· Test-Device description.
· Detailed technical proposal, including details specified in this document.

· The optional requirements listed in the technical specification document shall be technically fully responded to (and will be included in the filtering procedure).

· Technical specifications.
· Operator manuals.
· Maintenance plan and manuals (including periodical and preventative maintenance).
· Cost proposal, in Israel Shekel, for the proposed project as outlined in Appendix B of the RFP, including:

· Purchase price for the project 

· Full Maintenance (extended warranty), on yearly basis for 10 years (not including the warranty period) 

· Optional requirements, listed in the technical specification document (requested by the Client), shall be priced and, in case purchased, will be weighted.   

· Additional information as requested in this SOW.

b. The proposals will be submitted in five (5) hard copies and two (2) CDs (MS Office). Mailed – on proposal submission final date.
2.1.4 Proposals filtering - EC's responsibility.
2.2 Phase 2 - Proposal Evaluation and Performance Verification

Tasks comprising project’s phase 2 are specified including the corresponding responsibilities as follows:

2.2.1 Proposal Evaluation - EC's responsibility
2.2.2 Verification Tests - Contractor’s and EC's responsibility

2.2.2.1 Objective: To verify that the proposed systems, withstand all Contractor’s declarations regarding system performance.

2.2.2.2 Verification tests shall be conducted only for the Contractor with highest scores after technical evaluation.
2.2.2.3 Verification tests shall be conducted on the Contractor’s premises or at an operational site. The procedure consists of the Contractor’s staff operating the system and obtaining the best possible screening images to be evaluated by the EC.
2.2.2.4 The EC may decide to conduct only parts of the tests.
2.2.2.5 Aspects to be tested:

System performance will be tested regarding mandatory requirements and Contractor’s declaration in the following parameters:

· Screening range: For the screening process, the cargo will be loaded on trucks in order to confirm system's ability to image the required objects.

· System performance in parameters of:

· Penetration.
· Resolution.
as specified in Section 5.

The above-mentioned parameters will be tested in the nine (9) defined positions as specified in Section 5.
· System throughput

· Material discrimination capabilities 
2.2.2.6 After completing the required Verification Tests, the contractor may demonstrate additional system capabilities. The demonstration of these features will be performed in coordination with the EC and within schedule constraints.
2.2.2.7 Contract award
2.3 Phase 3-Systems Reviews and manufacturing - Contractor’s responsibility.
This phase will comprise of project reviews and system manufacturing.
2.3.1 General

2.3.1.1 The Contractor shall present systems design reviews to the Client.  Technical and management (timeline) issues shall be presented, showing in detail the schedule and implementation to be achieved in all aspects of the SOW.

2.3.1.2 All reviews shall be carried out in Israel, on the Contractors offices and/or at the site in coordination with the Client / CR.

2.3.1.3 The carrying out of Reviews and their precise date will be coordinated with the Client / CR. The reviews will not be held on Israeli Holidays.

2.3.1.4 The Reviews shall include all the components of the upgrading project, either of the buildings, systems or equipment installed at the site.

2.3.1.5 The Contractor must submit the Client a list of all personnel he intends to employ on site (including designers and sub Contractors), for approval, at this stage. Unapproved personnel will not be an excuse for the Contractor for any time delay.

2.3.1.6 The relevant documents for the reviews should be submitted to the Client / CR not later than 10 days before the date set for each review.

2.3.1.7 Full participation of all the designers and sub Contractors is required. 

2.3.1.8 Not later than two (2) weeks after completion of each Review, the Contractor shall submit the minutes of the meeting.
2.3.1.9 Design Approval

The approval which will be given to the design by the Client/CR, will not release the Contractor from the responsibility for his design, neither shall such approval release the Contractor from any liability placed upon him by provisioned in Form of Contract.

2.3.1.10 Quality Assures System

The Contractor shall submit detailed Quality Assurance plan of the entire program detailing how the Quality Assurance system of the Contractor is applied to the specific tasks. 

2.3.1.11 Work Plan and Time Schedule

At each Review the Contractor will present an Updated program work-plan, including: revised management plan, detailed Work Breakdown System, detailed schedule, milestones and status reports organization - in comparison to project's GANTT.

2.3.1.12 Final approval of the Contractor's designers and subcontractors will be given in the PDR.
2.3.2 Preliminary Design Review (PDR) - Contractor and Client responsibility
PDR will comprise of four (4) main parts, related to the following subjects:

a. The Intermediate screening system (including deployment in the site).

b. New radiography system. 

c. Site and Building construction.

d. Command, Control and Computer systems (Traffic Control, Safety and Security subsystems).

The various PDR meetings, relating to the various subjects, may be conducted successively.

2.3.2.1 General

e. The Contractor shall present a Preliminary Design reviews (PDR) to the Client. The PDR shall cover all issues presented in the proposal together with all changes anticipated in the planning. A paragraph-by-paragraph specification and contract review shall be presented with all technical or schedule problems identified. The reviews shall describe the specific equipment design, site's works, adaptations which the Contractor intends to implement.

f. The PDR meeting, based on Contractor's proposal, will be conducted no later than 3 weeks AEDC. The Contractor will submit the material to be presented at the PDR meeting no later than 1 week before the meeting. The material will be submitted via Email and two (2) CD's. 
2.3.2.2 Preliminary Design Review for the Intermediate X-Ray System (PDR - a)
2.3.2.2.1 The Design Review for the proposed Intermediate X-Ray System will be conducted no later then 3 weeks AEDC.

2.3.2.2.2 The following subjects will be included in the Review related to this x-ray inspection system:

1. X-Ray inspection system: Technical descriptions of the design, including geometrical and operational considerations, stability solutions, etc.

2. Imaging system: detector’s parameter specification

3. Scanning system: Description and relevant parameters: velocity, stability, flexibility.

4. System Performance

5. Radiation Safety: requirements, design, implementation in the site, including detailed calculations of the required shielding and documents required for licensing.
Note: It's reasonable to assume that, taking into consideration the dimensions of site's unoccupied area shielding walls will be required.
6. Image Workstation: operation, image evaluation, image enhancement, etc.

7. Operation: Check-in/out Workstations, registration, communication, etc.

8. Command and Control: System operation adapted/integrated with Site operation.

9. Maintenance: Contractor's preparation to provide the required maintenance (technician on site, critical parts to system operation, etc).
10. Computer: architecture, Data base and archive module.
11. Deployment; Contractor's plan and preparations to accomplish the site adaptation, required Infrastructure, operational procedures, safety.
12. Detailed review of all auxiliary systems and sub systems.
13. Electrical, hydraulic, communication, transportation, etc if required: standards in accordance to Israeli certification.
14. Implementation Time Line.
15. Training.
2.3.2.2.3 No later than four (4) weeks after review completion, the Contractor shall submit final documents for written approval, updated according to the Client representative's remarks at the review meeting.

2.3.2.3 PDR - New Radiographic system (PDR-b) - Contractor and Client responsibility.
2.3.2.3.1 The Design Review for the proposed new X-Ray System will be conducted no later then 3 weeks AEDC.
2.3.2.3.2 The following subjects will be included in the Review related to this x-ray radiography system:

a. X-Ray inspection system: Technical descriptions of the design, including geometrical and operational considerations, stability solutions, etc.

b. Imaging system: detector’s parameter specification
c. Scanning system: Description of the proposed scanning system, equipment specifications, control system, operation, maintenance and relevant parameters: control, velocity, stability, flexibility.

d. Performance: System Radiographic Performance, throughput, additional options.

e. Radiation Safety: requirements, design, detailed calculations and documentation required for licensing, safety plan prepared by authorized radiation safety Israeli consultant
f. Workstations: System Operator, Receptionist
g. Image Workstation: operation, image evaluation, image enhancement, etc.

h. Operation: Check-in/out Workstations, registration, communication, etc.

i. Command and Control: System operation, Site operation, etc.

j. Computer: architecture, Data base and archive module.
k. Deployment; site adaptation, required Infrastructure, operational procedures, safety.
l. Detailed review of all auxiliary systems and sub systems.
m. Electrical, communication, etc: 
n. Maintenance: plan, critical parts to system operation.

o. Implementation Time Line.
2.3.2.4 PDR - Site and Buildings (PDR-c) - Contractor and Client responsibility
2.3.2.4.1 The Preliminary Design Review for proposed changes in the site and buildings required as result of the upgrading process will be conducted no later then 3 weeks AEDC.

2.3.2.4.2 The following subjects and the relevant documents will be presented in the Review related to this upgrading: 

a. General and basic plans scaled to 1:50 minimum. 

These plans shall specify dimensions, equipment and materials to be used and full description of the solutions.

b. All drawings shall be prepared in the metric system of measurement (MKS).

c. Basic plans for Site main gates, pedestrian's gate and crosswalk as well as the operators cabins at the gates (to contain the new control systems)  

d. Basic solutions for the incorporation and adaptation/installation of electrical power supply system, fire detection, air conditioning system etc;

e. Updated and detailed time schedules for the design, supply and implementation of the works.
f. The time schedules shall include milestones for progress of the work and shall show in detail how the Contractor intends to adhere to the time schedule for timely completion of the works.

2.3.2.4.3 Technical Documents Content

1) Site design changes;

2) Connection to existing infrastructures;

3) Power system design;

4) Air conditioning system design;

5) Communication system design;

6) Fire detection and extinguishing system;

7) Security and CCTV systems;

8) Sanitary systems;
2.3.2.5 PDR for the Systems (Command and Control, Computer, etc.) - (PDR d) Contractor and Client responsibility.
2.3.2.5.1 PDR for the proposed systems will be conducted no later than 3 weeks AEDC.

2.3.2.5.2 At this stage the contractor shall present basic design for the following systems:

g. Security and CCTV systems 

h. Traffic control system (TCS)

i. Communication systems

j. PA

k. Traffic lights, signposts, etc.
2.3.2.5.3 Technical descriptions, design principles and basic solutions for the incorporation and installation of the various systems will be presented.
2.3.2.5.4 The Contractor shall present, for customer approval, detailed system acceptance test protocol for each system.  

2.3.3 Detailed/Critical Design Review (DDR/CDR) - Contractor and Client responsibility

2.3.3.1 General

2.3.3.1.1 The Contractor shall present a Detailed Design Review (DDR) to the Client.  The reviews shall cover all issues presented in the PDR together with all changes anticipated in the planning. A paragraph-by-paragraph specification and contract review shall be presented with all technical or schedule problems identified.  The Review shall describe the specific equipment design, which the Contractor intends to implement.  

2.3.3.1.2 DDR meetings will be conducted not later than:

l. DDR - a, Intermediate screening system - 10 weeks AEDC.
m. DDR - b, New Radiographic system - 17 weeks AEDC.
n. DDR - c, Site and building construction - 21 weeks AEDC.
o. DDR - d, Control and Security systems - 21 weeks AEDC.
2.3.3.1.3  No later than three (3) weeks after the Review completion, the Contractor shall submit, for final written approval, a Final documents, updated, according to the Client/CR's remarks at the Review meeting.

No further design changes shall be authorized after the final Review without a written change order or approval issued by the Client.

2.3.3.1.4 Each document shall be submitted in four (4) copies.

2.3.3.1.5 Full participation of all the designers and sub Contractors is required.

2.3.3.2 Detailed Design Review (DDR - a)

2.3.3.2.1 DDR/CDR for the Intermediate radiography system will be conducted no later than 10 weeks AEDC.

2.3.3.2.2 All subjects presented at the PDR will be detailed in the presentation of the CDR for the x-ray inspection system, including:

p. X-Ray inspection system.
q. Imaging system.
r. Scanning system.
s. Radiation Safety. 

t. Workstations: presentation of the operational procedures incorporated in the site for the workstations:

· Check-in operator.
· Image operator.
· Data Base and Archive.
u. Computer systems.
v. Project Time Table.
2.3.3.2.3 Operation: Radiation Safety and traffic control aspects that require site adaptation will be presented. 

2.3.3.3 Detailed Design Review – New x-ray system (DDR - b)
2.3.3.3.1 DDR for the new radiography system will be conducted no later than 17 weeks AEDC.

2.3.3.3.2 All subjects presented at the PDR will be detailed in the presentation of the DDR for the x-ray inspection system, including:

w. X-Ray inspection system.
x. Imaging system.
y. Scanning system (Design and Control).
z. Radiation Safety. 

aa. Workstations: presentation of the operational screens incorporated in the site for the workstations:

· Check-in/out operator.
· Image operator.
· Data Base and Archive.
· Manual site operator.
ab. Computer.
ac. FAT Protocol: A detailed description of the Factory Acceptance Test planned for the inspection system.

ad. Time Table.
2.3.3.4 Critical Design Review for the new X-Ray System (CDR –b)
2.3.3.4.1 CDR for the radiography system will consist of the Factory Acceptance Tests (FAT) and will be performed not later than 26 weeks AEDC
2.3.3.4.2 The CDR for the X-Ray system will be carried out at Contractor’s factory or installation in order to confirm contractor’s declarations in the proposal regarding system performance
2.3.3.4.3 The tests will be carried out according to the test plan submitted at the DDR meeting and confirmed by the Client 

2.3.3.4.4 The tests will be performed for the final radiography system / subsystems manufactured by the contractor, prior to its installation on the site. 

2.3.3.5 DDR construction (DDR/CDR- c) 

2.3.3.5.1 For this stage, the designers of the awarded Contractor shall prepare detailed plans following the approved preliminary design.

2.3.3.5.2 Client guidelines shall be given in Client's office. 

2.3.3.5.3 Schedule delays

It is hereby clarified that in case the Contractor does not meet the schedule and/or any stage of the schedule, the delay time shall not be deducted from the schedule of the project implementation.

2.3.3.5.4  Design Documents to be submitted at the DDR
The drawings and documents that the Contractor shall submit include, but are not limited to the following:

· Site Earthworks drawings

· Architectural drawings, scale 1:50 + sections and front views 
· Architectural details + furniture for all buildings

· Outdoor and indoor systems + equipment for all buildings

· Data sheets, catalogs, manuals

· Drawings and descriptions of all systems including radiography, mechanical system, control, communication, etc.

· Detailed drawings of all electromechanical systems, piping, electricity, air-conditioning, etc

2.3.3.5.5 Total schedule for approval of planning and drawings: 17 weeks.

2.3.3.6 Critical/Detailed Design Review for the Systems (DDR/CDR-d) 

2.3.3.6.1 At this stage the contractor shall submit detailed design of control, safety and security systems planned to be incorporated in the facility, operational procedures, interfaces and data flow.

2.3.3.6.2 The contractor shall submit equipment specifications, data sheets, invoices and supplier names regarding each system.

2.3.3.6.3 DDR for systems will be no later than 21 weeks AEDC.

2.3.3.6.4 CDR for the TCS (Traffic control), database and archive systems will be conducted and tested not later than 26 weeks AEDC following test protocol submitted by the contractor at the DDR meeting and approved by the Client. 

2.3.3.6.5 Upon successful completion of Factory Acceptance Tests, Client/CR approval regarding the system will be given.
2.3.3.6.6 Documents approval by the Client

The Contractor's attention is called to the fact that the Client reserves the right not to approve documents and drawings mentioned above if they do not meet all the requirements of this SOW. In such a case, the Contractor shall be required to make all the corrections and modifications required by the Client/CR and re-submit the documents for approval.

All the documents, drawings, etc., after being approved shall be attached to the contract and form an integral part thereof.

The implementation of the work shall start only upon the completion of the detailed design process and drawing approval as stated above.

2.4 Phase 4-Implementation - Contractor’s and Client's responsibility 

This phase comprises of the following parts:

2.4.1 Meeting and reports

2.4.1.1 Weekly meeting 


Weekly meeting at the site shall be coordinated with the presence of Contractor's project manager/representative and Client's representatives.  


At the meeting project progress will be presented and addressed.
2.4.1.2 Monthly Progress Report


The Contractor shall provide a monthly progress report describing the technical, schedule and management issues, the status of major subcontractors’ operations and significant future milestones.


Every third month, the Contractor shall include the following additional information in the monthly report:

ae. Program summary narrative to date.

af. Configuration status report.

ag. Significant technical, implementation and design data, including internal test reports of components and system.

ah. Subcontractors' progress and delivery states.

ai. Update milestone schedule.

The monthly program report will include GANT diagrams reports produced by a common computerized project - managing program, describing planed program against actual status. 

2.4.2 Installation of the Intermediate screening system - Contractor’s responsibility


Shipment, delivery and Installation of the Intermediate screening system in Ashdod site - are Contractor’s responsibility. 
2.4.2.1.1 System certification

2.4.2.1.2 System certification and obtaining all the necessary permits for operational service from all relevant Israeli authorities (radiation safety, electrical, hydraulic, communication, transportation etc.) are Contractor's responsibility.

2.4.2.1.3 The Contractor shall complete all the procedures and certifications required in Israel, including Supplier's A.T.P., authorized laboratory radiation safety inspection, electrical and transportation approvals, etc.

2.4.2.1.4 It is emphasized that obtaining of all permits and licenses required for system operation is solely the Contractor’s responsibility and should be performed by the Contractor, at Contractor’s expense.

2.4.2.1.5 Any adaptation in site's area required in order to properly operate the system as part of the Ashdod facility (Temporary fence, temporary gates, check-in cabins, shielding, parking etc.) shall be performed by the Contractor, at Contractor’s expense.

2.4.2.1.6 Any additional equipment and installations that will be required by Israeli law and regulations (safety barriers, extra warning lights, etc.), will be supplied by the Contractor, at Contractor’s expense,
2.4.2.2 Acceptance tests - Contractor's and Client responsibility
2.4.2.2.1 On completion of the installation of the screening system and auxiliary equipment (controls, fence, safety apparel, etc.) acceptance tests will be conducted by the Client/CR.

2.4.2.2.2 The Contractor shall submit to the Client a complete Plan and procedures for carrying out a full test of the systems and equipment parts at least two weeks before they are due to be implemented.

2.4.2.2.3 The Test Plan and procedures should be approved and signed by the Client/CR.

2.4.2.2.4 The Contractor shall inform the Client when all the work has been completed and the system is calibrated and ready for inspection.

2.4.2.2.5 The Acceptance Test shall begin no later than 5 working days from receipt of the Contractor’s notification. The examination shall be performed in the presence of the Contractor’s authorized representative.

2.4.2.2.6 A list of defects (if any) will be recorded in the Minutes and Reports of the Tests. The Contractor undertakes to repair these defects within a reasonable time from the time the list is delivered in a manner that will not delay the operational deployment of the system in the site.

2.4.2.2.7 Upon completion of the repairs, another examination will be made and should the results of the examination be in accordance with the defined requirements of this SOW and the Test Plan, the final tests shall be completed and the operational period shall commence.
2.4.2.3 Technical Documentation

2.4.2.3.1 The Contractor will supply a full set of operation manuals with the system, English and Hebrew versions (Hard- copies).

2.4.2.3.2 The Hebrew version of the operation will be presented to the Client for approval prior delivery of the system.

2.4.2.3.3 The manuals will be edited in MS Office format and shall contain all the required information regarding the different system operators (ex: safety, system operator, Image analyst, Check- In, Archive handling, traffic coordinator etc).
2.4.2.3.4 The manuals will be in a high quality color printing and will be bounded in a protective cover. The manuals will include photos and diagrams that will demonstrate proper operation of the different sub-systems.

a. Additional 3 hard copy sets of the Hebrew/ English versions will be provided.

b. Additional 3 soft copy sets, MS Office format, of the Hebrew / English versions will be provided.

2.4.2.4 Training (Intermediate System)
2.4.2.4.1 The Contractor shall perform System Training courses in Israel. The Contractor will specify the course content and aids. The Contractor will submit course materials, for approval by the Client/CR, at least four weeks before course beginning. 
2.4.2.4.2 The Contractor shall train Client's operators to operate the system, paying attention to all aspects of operation: functional, radiation safety, mechanical safety, image analyzing, troubleshooting etc. The Contractor shall present the system overview “top down”, (including operational concept, maintenance etc).

2.4.2.4.3 The training will be composed of both theoretical sessions and practice of the system operation and image analysis.

2.4.2.4.4 The technical literature for the training shall include at least the following:

(
Operator’s manual, including operation verification procedure required, with the system delivery.
(
CD-ROM containing the operator’s manual (MS Office Word).
2.4.2.4.5 The course will end with a final certification test.

2.4.2.4.6 Operators that passed the training course and tests successfully will be certified by the Contractor to operate the system.

2.4.2.4.7 Three (3) Operators Training sessions will be conducted, each session of up to 16 operators. 

2.4.2.5 Intermediate system Operation

2.4.2.5.1 The Contractor is responsible that, after the final acceptance the system and the supplied auxiliary equipments, have all their parts functioning and that their performance is in accordance with the requirements detailed in this SOW and/or in the contract proposal and undertakes that the equipment shall be free of any damage and that it is operational according to the required specifications and standards.

2.4.2.5.2 The Contractor is responsible and will repair and/or replace any part in which a defect is detected within the operation period from the acceptance tests of the system until the new radiography system passes acceptance tests and is operational.

2.4.2.5.3 Intermediate system's maintenance, including the on-site technician, during its operation is part of the project and Contractor's responsibility.

2.4.3 Installation of the New Systems - Contractor's responsibility
This phase comprises of the following parts:

2.4.3.1 Site works 

Implementation of the changes / adaptation's works on the site 
2.4.3.1.1 Any adaptation in site's area required in order to properly operate the system as part of the Ashdod facility (Temporary fence, new check-in cabins, parking etc.) shall be performed by the Contractor, at Contractor’s expense.

2.4.3.1.2 The Contractor shall implement all the civil works needed in order to fully operate all the equipment, according to the SOW. All civil works shall be conducted after receiving the Client's/CR approval to the plans. 

2.4.3.2  Dismantling works - Contractor's responsibility

All dismantling works, including the removal of the existing radiography systems will be executed as required by the Israeli laws and recycling regulations (including providing and receiving all of the required approvals and certifications from the relevant authorities). These works are solely Contractor's responsibility and shall be performed only by the Contractor and at his expense.
2.4.3.3 New systems installations


Shipment, delivery, Customs clearance and Installation of the New systems, including all auxiliary equipment, in Ashdod site - are Contractor’s responsibility. 
2.4.3.4 System certification

2.4.3.4.1 System's certification and obtaining all the necessary permits for operational service from all relevant Israeli authorities (radiation safety, electrical, hydraulic, communication, transportation etc.) are Contractor's responsibility.


The Contractor will obtain all the necessary permits for operational service of the systems from all relevant Israeli authorities prior the acceptance tests for each system and subsystem.
2.4.3.4.2 The Contractor shall complete all the procedures and certifications required in Israel, including Supplier's A.T.P., authorized laboratory radiation safety inspection, electrical and any required approvals, etc.


It is emphasized that obtaining of all permits and licenses required for systems operation is solely the Contractor’s responsibility and should be performed by the Contractor, at Contractor’s expense.

2.4.3.4.3 Any additional equipment and installations that will be required by Israeli law and regulations (additional safety equipment, extra warning lights, etc.), will be supplied by the Contractor, at Contractor’s expense,
2.4.3.5 Preliminary Acceptance tests 


On completion of the installations of the equipment preliminary acceptance tests will be conducted by the Contractor for each of the systems. 

2.4.3.5.1 The Contractor shall submit to the Client/CR a complete Plan and procedures for carrying out a full test of the systems and equipment parts at least two weeks before they are due to be implemented.

2.4.3.5.2 The Test Plan and procedures, as defined in this SOW, should be approved and signed by the Client.

2.4.3.5.3 Regarding each system, the Contractor shall inform the Client/CR when all the works have been completed and the systems are calibrated and ready for inspection.

2.4.3.5.4 The Preliminary Acceptance Tests will be performed by the Contractor. Tests results, for each system, will be submitted to the Client/CR. 

2.4.3.5.5 A list of defects (if any) will be recorded in the Minutes and Reports of the Tests. The Contractor undertakes to repair these defects within a reasonable time from the time the list is delivered in a manner that will allow an acceptable operation of the systems during the test run of site facilities.

2.4.3.6 Site Test Run

2.4.3.6.1 After successfully passing the Preliminary Acceptance Tests (performed by the contractor) the site will be run for one month by and under the responsibility of the Contractor
2.4.3.6.2 During that period the customer's staff will undergo a training course.

2.4.3.7 Training 

The Contractor shall perform training courses for systems operators, image analyzers, first level maintenance, Radiography system instructors, etc.
2.4.3.7.1 The Contractor will specify the course content and aids. The Contractor will submit course materials, for approval by the Client/CR, at least four weeks before each course beginning.

2.4.3.7.2 The Contractor /Supplier of each system will provide a full training course for operators as well as level1 maintenance, as defined for the systems in the relevant sections. The Contractor shall present the system overview “top down”, (including operational concept, maintenance etc).

2.4.3.7.3 The Contractor/Supplier shall train Site operators to operate the systems, paying attention to all aspects of operation: functional, radiation safety, mechanical safety, image analyzing, troubleshooting etc.

2.4.3.7.4 The Radiography system training will be composed of both theoretical sessions and practice of the system operation and image analysis.

2.4.3.7.5 Course materials to be submitted will include all instructor frontal presentations, trainee literature, certifications tests as well as the practical exercises. All materials will be provided on digital media (MS Office) and three (3) hard copies.

2.4.3.7.6 The technical literature for the training shall be included comprising of at least the following:

(
Operator’s manual, including operation verification procedure required, with the system delivery, English and Hebrew versions.

(
CD-ROM containing the operator’s manual (MS Office Word).
2.4.3.7.7 The radiography course will end with a final certification test.

2.4.3.7.8 Operators that passed the training course and tests successfully will be certified by the Contractor to operate the systems.

2.4.3.7.9 Four (4) Operators (all functions) Training sessions, each session of 16 operators, will be conducted. The Client will set the date for the last (4-th) session – up to one year following the date of first session. 
2.4.3.7.10 Maintenance training sessions

2.4.3.7.11 In addition to operators training, the training sessions in this phase shall include “Level 1” Maintenance training for basic knowledge only.

2.4.3.7.12 Instructor Training session

 One (1) instructor training course (covering all training) designated to prepare Israeli instructors to instruct and train additional Israeli operators and instructors will be conducted.
2.4.3.8 Dismantling the Intermediate system and recovering the site to the required condition.
2.4.3.9 Pilot  
The facility, including all new implemented systems will be run, for three additional months, by the customer's employees, under the supervision of the Contractor.
2.4.3.10 Final Acceptance Tests 

At the end of that Pilot period a Final Acceptance Tests conducted by the Client, will take place. 
On the successful completion of these tests a warranty period of one year will commence. 
2.4.3.10.1 The Final Acceptance Test shall begin no later than 5 working days from receipt of the Contractor’s notification stating the systems are ready for tests. The examination shall be performed in the presence of the Contractor’s authorized representative.

2.4.3.10.2 Upon completion of the tests and should the results of the examination be in accordance with the defined requirements of this SOW and the Test Plan, the final tests shall be completed and the warranty period shall commence.

2.4.3.11 Warranty Period - 1 year
2.4.3.11.1 The Contractor is responsible that, after the final acceptance, all the facilities, systems and equipment supplied within the contract, have all their parts functioning and that their performance is in accordance with all the specifications detailed in this SOW and/or in the contract proposal and undertakes that the equipment shall be free of any damage and that it is supplied according to all specifications and standards.

2.4.3.11.2 The Contractor is responsible and will repair and/or replace any equipment in which a defect is detected within warranty period from the final acceptance of the facility or according to an optional additional longer warranty period as specified in the contract.

3. Project Management – Guidelines

3.1 Project Manager

3.1.1 Project manager and his alternate shall be designated by the Contractor. 


The Contractor shall appoint a project manager to coordinate and check, on his behalf, all the planning work carried out by the Contractor. The project manager shall follow up all the planning stages, the approvals, implementation and overall supervision as the Contractor's representative.

3.1.2 The Contractor, at all times during performance of the contract and until the work is completed and accepted by the Client, shall directly superintend the work, or assign a superintendent, who shall have authority to act for the Contractor. 

3.1.3 Safety Officer
The Contractor shall appoint, in addition to the manager, a safety officer with a comprehensive knowledge and understanding of all local regulatory requirements relating to safety, health and environment.  The safety officer responsibilities shall include creating, maintaining and ensuring a safe working environment for all personnel in the site during the implementation of the upgrade project. The role also includes formulating operational procedures that recognize hazards.
3.1.4 Communication between the Customer and the Contractor and vice versa shall be conducted via the Project Manager or his alternate and them alone.

3.1.5 The Project Manager or his alternate must sign all the documentation submitted to the Client/CR.
3.2 Supervision by Client's Representative (CR)

3.2.1 The Client's representative, whose approval at each stage of the work shall be required, will perform on-site supervision. All work materials, manufacturing processes, and methods of construction shall be supervised and approved by the representative. 

3.2.2 The Client's representative may direct Acceptance of any material or workmanship or reject it if he finds either or both to be unsatisfactory.

3.3 Correspondence regulations

3.3.1 Unless otherwise specified, all documents mentioned in this document shall be submitted to the Customer/ CR.

3.4 Work meetings

3.4.1 The Customer may summon meetings with the Contractor within Client's facilities.

3.4.2 The Contractor is obligated to summon all relevant representatives needed (after approval by the Client), in addition to Client's representatives.

3.5 Management Plan


The Contractor shall submit a detailed management plan for the design, supply and the implementation of the Inspection Facilities. The plan shall be in the form of a “GANNT” chart.


The detailed implementation plan shall be integrated in the program’s master schedule and presented for customer approval.  

3.6 Designers, Manufacturers, and Subcontractor List

3.6.1 The Contractor shall submit a list of well-experienced designers, which he intends to employ in the different work stages, for Customer approval. The Contractor shall utilize designers that have proven history of working with The Israeli offices. The same shall apply to Sub-Contractors and manufacturers. Particularly, if required, the Architectural designer must be an Israeli based firm. All local participating firms shall be registered and approved suppliers. 
3.6.2 Special conditions

a. The Contractor must employ designers/consultants meeting applicable requirements of the Israeli laws, regulations and standards applicable to the project. Only those designers/ consultants will sign any plan submitted to the Client and Authorities.

b. The Contractor is responsible for the coordination of the overall planning and that he and his consultants and designers meet the schedules specified for the design.

c. The design and implementation details shall be approved by the Client before their implementation.

d. The Contractor shall carry out the planning stages in full coordination with the Client.

e. Documents, drawings and data sheets shall be submitted in three hard copies for comments.

3.6.3 Designers employed by the Contractor (in Israel)

3.6.3.1 All the planning inspection and work to be carried out by the Contractor according to this SOW shall be carried out by architects, civil engineers, electrical engineers, etc., whether they are self employed or Contractor's employees, this designers shall be qualified and licensed according to the applicable Israeli laws, regulations and standards having a professional experience of at least 5 years.

3.6.3.2 The project manager and the designers will be subjected to a security clearance and approval by the Client.

3.6.3.3 The agreement of the Contractor with the designers shall include, among others, a clear obligation of the designer towards the project manager and the Contractor to carry out the planning work at proper professional standards, according to the professional rules and the guidelines included in this SOW.

3.6.3.4 In addition, the agreement shall include visits of the designers to plants manufacturing items like steel structures, metal work, carpentry, aluminum parts, furniture, etc., for the project. General supervisory visits shall be coordinated with the Contractor's supervisor. The designer shall submit his comments on the visit to the supervisor in writing. Copies of periodic general supervisory report shall be kept in the site foreman's office at the plant for supervisor's inspection.

3.6.3.5 Collecting and keeping the reports and comments of the designers shall be the responsibility of the project manager. 

3.6.3.6 Official documents, required for submission to various authorities, should be prepared in Hebrew.

4. SOW Terms

4.1 Visiting the site and studying the work conditions


The site is located near Ashdod Port. The Contractor confirms that he is aware of the site conditions and accepts it as is. The work shall be carried out in full coordination with the Client (Customs), with Client's supervisor (CR) and approval of local Authorities.

4.2 Site cleanliness

4.2.1 Site cleanliness and garbage removal

4.2.2 The Contractor shall clean the work site from time to time and at Client supervisor’s demand and at least twice a month remove the garbage from the site, to a garbage disposal site approved by the proper local authority (no matter how distant) at his expense. It's emphasized that Ashdod site, being fully operational during project implementation phase, shall remain clean and no garbage disposal will be allowed at site's area, roads or parking lots.  
4.2.3 Removing digging material, dismantling materials, debris and garbage


The Contractor shall remove digging material, dismantling materials, including parts of the radiography system, used materials, debris and garbage of any kind, at his expense, out of the site, to a garbage disposal sites (no matter how distant) approved by the proper local authorities, according to safety regulations and  required obligating codes.


This instruction does not refer to dismantled materials that may be reused.

4.3 Work Safety 

4.3.1 Contractor shall furnish and construct all guardrails, fences trestles, tags, signs, shaft ways, false work and other temporary structures required to ensure the safety of all personnel on site at all times during the work.

4.3.2 A temporary 2-meter high metallic safety fence and gate shall be erected around the work areas with proper signs, and the entrance to each work site should be closed, according to the various work stages.


Upon the completion of the work, these fences shall be removed.

4.3.3 All expenses incurred for meeting safety regulation shall be on the Contractor.

4.3.4 Contractor shall be responsible for all injuries to persons or property of any kind whatsoever occurring due to these constructions.

4.4 Contractor's Organization in the site

4.4.1 The organization areas of the Contractor shall be in a location indicated by the Client. The Contractor shall receive, in advance, Client's approval regarding the location of the storage areas, equipment and materials warehouses and services. 

4.4.2 On the site, upon coordination with the Client, some customs offices and facilities (toilets, kitchenette etc.) in the radiography building may be used by the Contractor (for example the technician's office and the spare parts room).
4.4.3  It's emphasized that upon completion of works Contractor will assure that:

· The new/upgraded facilities shall be locked until accepted by the Client. 
· All offices used by the Contractor during the project will be cleaned and repainted before accepted by the Client.
4.5 Avoiding interference

4.5.1 The Contractor's attention is called to the fact that during the implementation of his work in the site, meaning the installation of the new, main radiographic system the ongoing activities in the site must continue, including possible temporary facilities at or near the work site. 

4.5.2 Not only that the Contractor shall not interfere with these activities and shall carry out his work with maximum consideration and cooperation, but he shall install a temporary screening system at the site to provide the necessary means for cargo inspection. 

4.5.3 The requirement to avoid interference shall not constitute a cause for any claim by the Contractor to extend the time schedule for the project implementation or any other claim.

4.5.4 The Contractor undertakes not to place materials and equipment on the public access road to the site and to conduct his work without obstruction of any sort to vehicular and pedestrian traffic.

4.5.5 The Contractor shall take all possible steps and at his own expense to give warning to prevent any disturbance including signal lamps, flags, etc. as required by law.

4.6 Access to / in the site area

4.6.1 The Contractor's work within the site shall be limited to work sites only. 

4.6.2 The access routes to and from the work site shall be coordinated with the Client. Any damage caused to existing roads and/or platforms shall be repaired immediately by the Contractor to the full satisfaction of the supervisor.

4.6.3 In order to enable direct access to site's area, additional temporal gate may be opened, if required, in the perimeter fence. At the end of works it's Contractor's responsibility to close the gate and return the fence to its original condition. 

4.7 Contractor's responsibility 

4.7.1 The Contractor shall ascertain in advance the presence of various facilities, systems and infrastructures in the various work parts.

4.7.2 The responsibility to avoid damage to the facilities shall be the Contractor's solely. In case of damage, the Contractor shall repair them at his expense, even when locations were indicated on the drawings.

4.7.3 The contractor will be held responsible for any damage to the facility and the equipment installed and/or stored in it, until successful completion of the final acceptance test and handing over the complete facility. Any damage resulting from the above will be repaired by the contractor and solely at his expense.

4.7.4 The contractor will be held responsible for damage to any person working or visiting the facility, until successful completion of the final acceptance test and handing over the facility to the Client. The contractor shall have valid insurance policy covering employees as well as third party.

4.8 Project Documents

4.8.1 Contractor's responsibility for planning documents

4.8.1.1 The approval of the drawings by CR on behalf of the Client at any stage will not absolve the Contractor of his full responsibility for the contents of the documents, the design quality, static calculations and other documents submitted for Client approval. CR's approval will not absolve the Contractor in respect of mistakes, inaccuracies and errors in the calculations, if such mistakes, inaccuracies and errors are detected.

4.8.1.2 Any damage resulting from the above will be corrected by the Contractor, and solely at his expense.

4.8.2 Delay in submitting documents

4.8.2.1 Contractor's delay in submitting documents for Client's approval beyond schedule shall not constitute a cause for a claim by the Contractor to extend the time allocated for the project implementation.

4.8.2.2 In addition, if the drawings are submitted on time but are rejected by the Client or by CR, returned to the Contractor and re-submitted for approval, no claim to extend the planning and implementation period of the project will be accepted and this delay will not constitute a cause for canceling delay liquidated damages.

4.8.3 Conflicting documents

4.8.3.1 In any case of conflict between the text of the specification and the text of a drawing, whether CR's or Contractor's, and in any case of conflict between any document of this SOW and another document referred to in the contract, the Contractor shall notify CR in writing and report on such a conflict within 7 days from its detection.

4.8.3.2 CR will instruct the Contractor in writing with respect to the conflict and/or clarify the uncertainties, regarding the prevailing interpretation.

4.8.3.3 In case the Contractor will carry out the work which is the subject matter of said conflict, without CR's approval, all the modification and/or demolition work costs of the said part of the work and/or costs of any other action instructed by CR will be paid solely by the Contractor and no claim on the Contractor's side, due to said conflict and/or vagueness, etc., will be accepted.

4.8.3.4 Any drawing or list intended for implementation by the Contractor should be signed by the Client/CR and bear the date of approval.

4.8.4 Documents used in Contractor's project planning 

a. Project specifications.

b. Guideline drawings attached to the SOW.

c. General specifications of the inter-ministerial committee.

d. Israeli laws, regulations and Standards or applicable foreign standards, if there are no Israeli Standards.

e. Contractor's drawings, that received Client's approval for implementation, shall replace the guideline drawings noted in subparagraph b. above.

4.9 Implementation

4.9.1 Stages of implementation


The work, the subject matter of this SOW, shall be executed simultaneously in all site parts. However, Client/CR is entitled to set the work implementation order according to his priorities. The Contractor shall not be entitled to any extra payments for setting the order of priorities for implementation by the supervisor.

4.9.2 Disagreements during Implementation of the Work 


In case of disagreement during changes implementation regarding interpretation of drawings, the final binding decision will be made solely by Client/CR.

4.9.3 Supervision of Implementation of the Work 


The supervisor on behalf of the Client (CR) will monitor the implementation during the entire work period. CR supervision will be in full coordination with the contractor's implementation representative and contractor's work supervisor (the implementation engineer).

4.10 Responsibility for existing buildings and infrastructures

4.10.1 The Contractor shall be responsible for the integrity of existing roads and infrastructures in the site or adjacent to the site and shall repair, at his expense, any damage that may have been caused to them as a result of his work. Upon detecting any underground facility during the work, the Contractor must at once notify the supervisor and receive his instructions as to how to proceed.

4.10.2 Before digging, either manually or with a machine, works manager and Contractor's supervisor should be provided with all relevant information regarding machine's operation. It's Contractors responsibility to investigate and ensure there are no underground infrastructures in the digging lines as, but not limited to the following:

a. Telephone and Communication cables.
b. Electrical cables.
c. Water and sewer pipes.
d. Fuel and gas lines.
4.10.3 The Contractor is responsible for any damage caused to existing buildings and facilities. It's the responsibility of the Contractor to repair them at his expense to previous condition and to the full satisfaction of the Client and the supervisor, even when not indicated on the drawings. The repair should be made as soon as the damage is detected, at a time specified by the supervisor to avoid any obstruction of the ongoing activities at the site. 

4.10.4 Water and electricity

4.10.4.1 The site is connected to water and electricity sources. 

4.10.4.2 The water and electricity connection points and requirements shall be determined during the Contractor's tour of the site. The water supplied to the Contractor shall be for work purposes only. Client shall not be liable for interruptions in electricity and/or water supply, and the Contractor is responsible for making proper advance preparations to overcome such water and electricity interruptions (generators, etc.).

4.10.5 Radio and Telephone

4.10.5.1 Radio and telephone communication equipment can be operated on the site. If required, the Contractor is responsible for obtaining permits/additional frequencies from the Ministry of Communication 
4.10.5.2 Ordering additional telephone line will be done by the constructor. 

4.11 Selection of Equipment

4.11.1 The equipment to be installed will be of a heavy duty, from a manufacturer having a duly authorized agent in Israel who can provide maintenance services and spare parts in Israel. The Contractor shall submit to the Client a list of the equipment to be installed in the building and receive approval with respect to the type of equipment.

4.11.2 All materials and equipment shall withstand harsh conditions. All surfaces shall be plated, galvanized and painted with special epoxy paint.

4.11.3 The Contractor shall submit to the supervisor a sample of the equipment and materials intended for installation in the building, and receive his approval before installation.

4.12 SOW Procedures

4.12.1 Ownership of the drawings


The parties agree that all the drawings provided by the Contractor shall be owned by the Client, which shall be allowed to use all or part of them for any purpose.

4.12.2 Ownership of the systems software.
4.12.2.1 The parties agree that all the software provided by the contractor shall be used by the Client on a royalty free license basic, which shall be allowed to use all or part of them free of any limitations.

4.12.2.2 After the completion of the installation and successful operation of all the software systems, the contractor shall hand over a full package of original licensed copies of all software implemented in the project and full package of updated backup for all the software used in the project. 

4.12.2.3 Software updates will be part of the service and maintenance contract and will be provided free of charge during the 10 years maintenance. The source of FCS software and all other subsystems will be provided to the Client on CD.

4.12.3 Facility "as made" plans
4.12.3.1 After the completion of his work, the Contractor shall hand over the original drawing sheets to Client/CR.

4.12.3.2 All drawings, according to which "the work" with all details and systems for all the building and the other works shall be executed, shall be signed by the contractor, in addition to the signature of the applicable consultants.

4.12.3.3 If the drawings are proprietary or protected by copyrights or patents, the Client will use these drawings with the Contractor's approval.

5. Contractor’s Quality Control System (CQCS)

5.1 General

5.1.1 The contractor shall establish a Quality Control System for the implementation of adequate inspection and tests of all work items, including subcontractors' works, to ensure conformance to applicable specifications and drawings in respect of the materials, workmanship, construction, finish, functional performance, and identification for facilities.

5.1.2 The contractor is responsible for the coordination and payment for all tests required to be performed during the quality control process or prior to final acceptance or any usable phase thereof.

5.2 CQCS Specific Requirements

5.2.1 The contractor’s Quality Control System (CQCS) is the means by which the contractor assures himself that his work complies with the requirements of the contract plans and specifications.

5.2.2 The contractor shall implement the CQCS immediately after commencement of work.


The controls shall be sufficient to cover all works, including both on-site and off-site manufacture and shall be keyed to the proposed implementation sequence.

5.2.3 The controls shall include as a minimum three phases of inspection for all definable phases as follows:

5.2.3.1 Pre-Inspection:

This inspection shall be performed prior to beginning of any work on any definable phase of the project, as shown in contractor’s schedule.


It shall include a review of contract requirements, a check to assure that all materials and/or equipment have been tested and approved, a check to assure that provisions have been made to provide required control testing; examination of the work area to ascertain that all preliminary work has been completed; and a physical examination of materials and equipments to assure that they conform to approved shop drawings or submitted data and that all materials and/or equipment are on hand.


The Client shall be notified in advance of the preparatory inspections and such inspection shall be made a matter of record.

5.2.3.2 Initial inspection

This inspection shall be performed as shown in the contractor’s schedule and as soon as a representative portion of the particular project phase has been accomplished and shall establish the acceptable standard of workmanship, including a review of control testing for compliance with contract requirements, use of defective or damaged materials, omissions, and dimensional requirements.

5.2.3.3 Follow up Inspection

This inspection shall be implemented daily to assure the continued compliance with the contractor’s requirements, including control testing, until completion of the particular phase of the project.

5.3 CQCS Plan


The contractor shall prepare, for customer approval, the CQCS plan that shall include the personnel, procedure, instructions, and records to be used. This document shall include as minimum:

a. 
The quality control organization (chart).

b. 
Qualifications of personnel.

c. 
Authority and area of responsibilities of quality control personnel.

d. 
Plan for accomplishing quality control inspections including that for subcontractors.
e. 
Detailed listing and designation of all tests to be performed.

f. 
Method of documenting quality control operations, inspections and testing.

g. 
An explanation as to how the quality control organization relates to other staff elements as regards shop drawing submissions, as built drawings, revisions to the contract and safety.

5.4 CQCS Organization


The contractor’s quality control organization shall be adequately staffed to perform the following tasks:

a. 
Conduct all phased inspection (preparatory, initial, and follow-up in accordance with paragraphs above.)

b. 
Perform all testing required under the technical specifications and provisions of this attachment.

c. 
Prepare weekly QC reports in accordance with required hereinafter.

d. 
Review and approve all shop drawings.

e. 
Inspect equipment as they are delivered on site to insure compliance with approved shop drawings and specifications.

f. 
Conduct off-site inspections of supplies and services to be incorporated into the work.

5.5 CQCS Report


The contractor shall submit a monthly QC report. The report shall contain a record of inspections and tests for all work accomplished since the previous report and shall include the following information for each activity in-progress:

a. Progress schedule activity identification and description, dates of the commencement and completion of each operation.  

b. Phases of implementation underway during the time frame of the report (i.e. adaptations, reviews, etc.)

c. Phase inspections (pre, initial, or follow-up) of manufacture, implementation and location of inspection and/or tests that were made.

d. 
Results of Inspections, including nature of deficiencies observed and corrective actions taken or to be taken.

e. Report of tests performed, including those specified, with the results including failures and remedial action to be taken.

f. Results of inspection equipment upon arrival at the site and prior to incorporation into the work for compliance with submission approvals, damage and proper storage. 

g. Off-site QC activities.

h. Instructions received from the Client.
i. Record of previous Client instructions, addressed and supervised by the Quality Inspector 
j. 
In all cases, the report must be verified and signed by the Quality Inspector appointed by the contractor. 

k. Safety Instruction.
6. Acceptance Tests and Documents

6.1 Acceptance Test Procedures and Tools (as defined in Section 5)
6.1.1 The contractor shall submit for approval the full acceptance test procedures and test tool design to be implemented in respect of all items and equipment required by the SOW specification and/or contract, signed by the contractor’s internal quality supervisor.  

6.1.2 The Client/CR may alter the proposed test procedures submitted for his approval by the contractor as well as add additional tests to those proposed, with the aim of ensuring full testing and compliance with requirements at the levels of both individual components and the entire system.

6.1.3 The test procedures supplied shall include a full set of technical testing tools required for the testing.

6.1.4 Technical specifications for testing each of the systems will be provided. These specifications will be approved by Client and serve as technical specifications during the final acceptance tests of each of the facilities. The specifications shall include operation and testing instructions written by the manufacturer of the equipment for each facility. These specifications should be submitted not later than one month prior to the completion of the work (i.e., implementation of the acceptance test) according to the schedule submitted by the Contractor.

6.2 Factory Acceptance Test of the radiography system (CDR - b)

6.2.1 The main objective of these tests is to measure system performance in order to confirm contractor's declaration in the proposal.
6.2.2 The tests, an integral and mandatory part of system implementation process, will be conducted according to Contractor's proposal, submitted at the DDR and approved by the Client.
6.2.3 The tests should be conducted using the designated Test Device, according to the definitions detailed in this document in section 5 Clause 10.
6.2.3.1 Radiographic performance


The following parameters will be measured at the 9 defined positions:

· Penetration.
· Wire IQI.
· Hole IQI.
6.2.3.2 Material Discrimination.
6.2.3.3 Conveyor tests. 
6.2.3.3.1 Special attention shall be given to scanning system tests. 
6.2.3.3.2 The test will include operational aspects, maximal load, weight, scan velocities, etc. 

6.2.3.3.3 The conveyor tests, an integral and mandatory part of system implementation process, will be conducted according to Contractor's proposal, submitted at the DDR and approved by the Client.
6.3 Final Acceptance Tests

6.3.1 General

6.3.1.1 The contractor shall submit the Customer a complete plan, test tools and Test Device description and procedures for carrying out a full test of the installation, the systems and installed equipment parts at least one month before they are due to be implemented.

6.3.1.2 The Test Plan and procedures should be approved and signed by the Client. 

6.3.1.3 The contractor shall inform the Client when all the work has been completed and the installation is ready for inspection.  This notification shall include a declaration on the part of the contractor that the installation is complete, that it has been calibrated and that it is ready for operation and is of a quality and performance as required by this SOW.

6.3.1.4 The Acceptance Test of the Client shall begin no later than 14 working days from receipt of the contractor’s notification. The examination shall be performed in the presence of the contractor’s authorized representative (Project Manager).

6.3.1.5 A list of defects (if any) will be recorded in the Minutes and Reports of the Tests. 

6.3.1.6 It's the contractor's responsibility to repair these defects within a reasonable time which shall be defined by the Customer.  
6.3.1.7 Upon completion of the repairs, another examination will be made by the contractor, and should the results of the examination be in accordance with the defined requirements of this SOW and the Test Plan, the final tests shall be completed and the warranty period shall commence.

6.3.2 Electric System Inspection

6.3.2.1 The electrical system shall be inspected in accordance with the Israeli Electrical Law and Regulations.

6.3.2.2 Inspection of the electric installations will be performed, in coordination with the Client, upon the completion of the electric system installations/changes and prior to the connection of the electric system to the electrical grid and before operating the electric system or any component of it, by a licensed  - certified electrician.
6.3.2.3 The inspection fee shall be paid by the Contractor. The Contractor shall provide all means and instruments necessary for the inspection.

6.3.2.4 The electrical installations shall be operated only after the approval of the inspector.

6.3.3 Fire detection and extinguishing system inspection

6.3.3.1 These systems shall be approved by the Standard Institute of Israel (SII) and shall be inspected and approved by the municipal fire and rescue services. 

6.3.3.2 The contractor shall submit the report to the customer and repair all the remarks, until final approval.

6.3.3.3 The SII and Firefighting Authorities Inspections shall be on the contractor expenses
6.3.3.4 The contractor will submit to the Client the official Firefighting Authorities' Approval confirming that the facility passed all tests and may start operation.  
6.3.4 X-Ray radiation safety inspection

6.3.4.1 The X-Ray systems safety shall be checked, and approved by all  the necessary official authorities  according to the Israeli law  and Regulations.

6.3.4.2 The contractor shall submit to the Client/CR the Official Radiation Safety Approval.

6.3.4.3 The contractor shall carry all the inspections and approvals expenses.

6.4 Factual (As Made) plans/ drawings 

6.4.1 The Contractor shall provide the following documents before final acceptance of the project:

6.4.1.1 The factual (As made) plans - depicting the actual final status, of the areas and buildings that were built or adjusted as part of this project

6.4.1.2 Plans of the following systems, newly installed or changed/upgraded /adapted shall be submitted:

a. Screening system.
b. Scanning system.
c. Computer systems.
d. Control systems, including TCS.
e. Safety and security systems (CCTV, etc).
f. Sanitation facilities.
g. Electricity and communication facilities.
h. Air conditioning facilities. 

i. Gardening and irrigation.
j. Site development, roads and sidewalks

k. Water lines, sewer pipes and ditches.
l. Sign system (standard, electronic, security and safety signs) 
m. Fire detection and extinguishing.
n. Gates area (Entrance and Exit)
6.4.1.3 These documents, depicting the actual status of the upgraded facility will be submitted in five copies and one set of originals and digital media. The originals will be those approved by the Client, signed by him and bearing the approval date

6.4.1.4 The factual drawings (depicting the actual status) referring to underground installations shall be prepared based on measurements of a licensed surveyor.


The supervisor shall approve the factual drawings depicting the actual status.

6.5 Facility manuals 

6.5.1 The submitted facility manuals shall be in Hebrew and English and shall include the following data:

6.5.1.1 Schematic diagrams describing each building with all internal and external systems, including a schematic diagram of the electrical board

6.5.1.2 Operation and maintenance instructions for each system, based on the manufacturer's instructions
6.5.1.3 Troubleshooting procedures for each system

6.5.1.4 Catalogs of all equipment items supplied, including mechanical and electrical systems.

6.5.1.5 A priced list of recommended spare parts for the systems, including catalog numbers, manufacturer's name, address of the manufacturer or his agent in Israel, and details that will enable the purchase of spare parts.

6.5.1.6 Operation and maintenance instructions of level A - Operator (detailed instructions and flowcharts accompanied by explanations by means of drawings to show commands, etc., including color photographs of all components of the equipment in their final location, the photography shall be made in coordination with the customer).

6.5.1.7 Training course Syllabus
6.5.1.8 Detailed preventive and periodic maintenance instructions, location and repair of breakdowns for each sub-system, including priced list of recommended spare parts..
6.5.1.9 Warranty certificates of the manufacturers of all systems installed in the building.
6.5.1.10 List of drawings for the whole project.
6.5.2 The manuals (English and Hebrew versions) will be submitted in five (5) hard copies, and two (2) on digital media. The hard copies will be bound in binders and/or standard files that will include a suitable folder for drawings.

6.5.3 Upon completing the preparation of the literature the Contractor shall deliver to the customer, 2 months before the acceptance tests, a draft for Customer approval in Email in two (2) hard copies and two (2) copies on digital media.
6.5.4 The submission of the above mentioned documents will be a precondition for project acceptance. No financial claims will be accepted with respect to the preparation of these documents.

6.5.5 All manuals and data shall be submitted in hard copies and Digital media. 
7. Operation, Service and Maintenance 

7.1 License and Permits

7.1.1 Safety

7.1.1.1 The Contractor is responsible for all safety aspects of the systems.

7.1.1.2 The Contractor shall tutor Customer operators, as needed, in all safety aspects required for systems operation.

7.1.1.3 The Contractor's representative in Israel shall be certified to work with high energy x-Ray accelerators, according to the Israeli law and regulations. The Contractor's representative in Israel shall have the licenses and permits to operate the system in their facilities and the ability to fully inspect, calibrate and service the system.

7.1.1.4 It is the Contractor's responsibility (schedules, payment etc.) to obtain all of the required radiation permits, to invite the authorized laboratory to certify the safety of all and any specific system, before any operation by Client can be performed during the whole process.
7.2 Training

7.2.1 The Contractor shall conduct the training at his expense. 

7.2.2 The training shall consist of orderly theoretical and practical ("hands-on") courses, four (4) sessions each of 16 operators and one instructors' session.
7.2.3 The object of the course is to train the operators to perform operation and level 1 maintenance activities for each system installed at the site. 
It's emphasized training the operators in maintenance topics is intended for general information only and site maintenance is solely Contractor's responsibility. 

7.2.4 Operators training shall be performed after preliminary acceptance tests.
7.2.5 The Contractor shall submit a list of Contractor's personnel and the functions they perform who will require instruction in the operation and maintenance of the various systems on the site. 

7.2.6 The Contractor shall perform any other activities required in order to conduct supplementary training.
7.2.7 Customer training program shall include theoretical and practical instruction, and shall inform the personnel of all information about the system and its operation.

7.2.8 The contractor shall submit the training programs for Client/CR approval, at least one (1) month before the training course.

7.2.9 Training programs shall be prepared for all systems operators: 

a. Image analyzers,

b. Radiographic system operators,

c. Traffic Control, 

d. Check-in/out operator,
e. Supervisor,
f. Instructor

7.2.10 Training program will include software package - training simulation. 
7.2.10.1 This simulator, installed as part of a stand alone workstation, will be designated for ongoing, offline training of image operators.
7.2.10.2 The training simulator will be based on a large archive of radiography images and image analysis software identical to the operational one.
7.2.11 The training activities shall be conducted in Hebrew and English at the inspection site in Israel. 
7.2.12 Training material as well as systems manuals shall be supplied in Hebrew, delivered in hard copies and on digital media. 
7.3 O&M (Operation and Maintenance) Documentation

7.3.1 The requirements contained herein are in addition to all shop drawing submission requirements stated in other sections of the specifications. The contractor shall include the provisions for all items required under this clause in all purchase orders and sub-contract agreements. Submissions required hereinafter will not absolve the contractor of any responsibility under the Warranty of Construction provisions of this SOW or under the various Guarantee clauses of the Technical Provisions.

7.3.2 Operation and maintenance (O&M) data

7.3.2.1 The contractor shall furnish O&M manuals for facilities constructed / adapted under this SOW, including grounds, buildings, mechanical, electrical, etc. The manuals shall be loose-leaf, indexed and shall consist of manufacturer's data sheets, manufacturer's operation and maintenance manuals, service and repair manuals, a schedule of parts replacement, catalogs, service bulletins, instruction charts, diagrams, manufacturer's recommendations for spare parts to be stored in the facility, detailed troubleshooting recommendations, a list of cleaning materials and other information, as necessary to support the operation, maintenance and repair of the end items of equipment, assemblies and systems.

7.3.2.2 Each facility shall be covered by a separate manual/ manuals consisting of all data pertaining to the equipment and/or systems within the facility. 
7.3.2.3 The contractor shall furnish five (5) hard copies of all O&M manuals to the Client, one CD and 1 set via Email not less than two (2) calendar months prior to contract completion. 
7.3.2.4 Failure of the contractor to submit complete O&M manuals within the aforementioned time period may result in a delay to the acceptance of the work for the full 2 months period after complete submissions have been accomplished. 
7.3.2.5 O&M data shall be in both English and Hebrew.

7.3.3 Supplementary data submissions

7.3.3.1 After the initial submission of Operation and Maintenance manuals and until final acceptance of all equipment, the contractor shall prepare and deliver the Client supplementary technical data as previously described for all changes, modifications, revisions and substitutions to equipment and components. 
7.3.3.2 For equipment or systems introduced into the contract under change order or modified by change order supplementary data shall be furnished within forty-five (45) calendar days after issuance of Notice to Proceed for the change order. The supplementary data furnished shall be properly prepared and identified for insertion into O&M manuals.

7.3.4 Framed instructions for systems

7.3.4.1 Approved wiring and control diagrams showing the complete layout of the entire system including equipment, piping, valves and control sequence, framed under glass or in approved laminated plastic, shall be posted, where applicable, in all mechanical equipment rooms. In addition, detailed operating instructions explaining safe start and stop procedures for all systems shall be prepared in typed form along the inspections required to ensure normal safe operation
7.3.4.2 Radiography Safety framed instructions will be provided according to the detailed specifications and approvals of the Client and the relevant Israeli authorities.
7.3.4.3 The instructions shall be framed as specified above for the wiring and control diagrams and posted beside the diagram. Proposed diagrams, instructions and other sheets shall be submitted for approval prior to posting. 
7.3.4.4 All framed instructions (operational, safety, etc.) shall be both in Hebrew and English. Operating instructions shall be submitted at least 30 days before acceptance testing of the systems and verified during acceptance testing.

7.3.5 Each measuring instrument (ammeter, voltmeter, pressure gauge, radiation detection etc.) shall be suitably marked to indicate the position of the indicator during normal operation.

7.3.6 Customer reserves the right to determine whether the above specified information as furnished by the contractor is adequate and complete and to require additional submissions by the contractor as necessary to ensure that adequate information has been furnished to provide for the satisfactory operation and maintenance of the various items of equipment and to fulfill the intent of the specifications. 
7.3.7 Additional submissions or re-submissions supplementing incorrect or incomplete data shall be made within thirty (30) calendar days after receiving notice by the Client/CR. All costs arising from these resubmissions shall be borne by the contractor.

7.3.8 All technical data contained in the manufacturer's catalogs and/or from the operating systems on site, shall be recorded on the Standard Technical Report forms, which shall be supplied by the contractor to the approval of Client/CR.

7.3.9 The contractor shall number and label accordingly all systems, equipment and accessories in accordance with the identification codes, which the customer/CR shall issue. Numbers and labels shall be assigned and fixed to those items of equipment and accessories, which have not been numbered on the contract drawings. The same system of numbering shall be used throughout, coordinating the numbers on the contractor's construction drawing with the operational and maintenance instructions and with the actual number on the equipment or accessory.

7.3.10 The contractor shall furnish, for every system and item of equipment and installation, technical material of the highest standard issued by the manufacturer including plans, catalogs and manuals for repair, operation and maintenance, alterations and a full list of parts and replacements that the manufacturer recommends should be kept in his local warehouse or in the project store. 

7.3.11 The contractor shall furnish full technical data for each system and item of equipment together with the design data for the start-up and operation. These shall be recorded so as to detail in full the capabilities of the equipment and systems.

7.3.12 Instruction and training for operation and maintenance


The contractor shall be responsible for the instruction and training of the operational and maintenance manual.

7.4 Warranty

7.4.1 The Contractor is responsible that, after the final acceptance, all the facilities, systems and equipment supplied within the contract, have all their parts functioning and that their performance is in accordance with all the specifications detailed in this SOW and/or in the contract proposal and undertakes that the equipment shall be free of any damage and that it is supplied according to all specifications and standards.

7.4.2 The Contractor will repair and/or replace any equipment in which a defect is detected within warranty period from the final acceptance of the facility or according to an optional additional longer warranty period specified in the contract.

7.4.3 The Contractor shall undertake during the warranty period of each one of the systems to continue to function in accordance with the data, the performance and the capabilities declared by the Contractor in his answers to this RFP.

7.4.4 In each case of malfunction, incompatibility and/or non-compliance with the provisions detailed above  the Contractor shall take immediate action upon receiving notice from the Client to remedy the malfunction and to bring the system to a working and operational capability in accordance with the data declared by the Contractor in his proposal.

7.4.5 Without prejudice to the aforesaid the Contractor shall supply comprehensive service and maintenance, during the warranty period without any additional payment to the purchase price. The service and maintenance will include labor, parts, and any other costs related to such a service and maintenance commitment. 

7.4.6 The Contractor shall provide a full-time maintenance employee available on the site during the warranty period for the site's standard operational hours (2 shifts). Services and work hours of the aforesaid maintenance employee will be given in the framework of the system maintenance at no additional cost.

7.4.7 The aforesaid service and maintenance shall be supplied in the framework detailed in the “Service and Maintenance” Paragraph 8.5 below of this SOW.

7.4.8 Despite the aforesaid provisions the Contractor will not be held responsible for damage to any parts of the systems and/or defects caused by use maintenance or operation of the system not according to the written instructions provided by the Contractor.


7.4.9 In addition to the aforesaid the Contractor will not be responsible for parts including software that were modified, altered, repaired or replaced by anyone other than the Contractor’s representative.

7.4.10 The warranty period shall include an unlimited working hours warranty for all buildings and systems installed on the site.

7.4.11 Response times required during the warranty period are identical to those defined in part 7.5 on service maintenance below.
7.5 Service and Maintenance

7.5.1 The Contractor undertakes to provide comprehensive service and maintenance for the systems for a period of at least 10 years from the end of the warranty period.

7.5.2 The maintenance shall be comprehensive for all systems and will include:

· On site maintenance employee (available during all site working hours, as specified here and after)

·  Preventive maintenance

·  Breakdown and faults repair including all of the spare parts.

The spare parts will be supplied by the Contractor on site free of any additional charge.

7.5.3 Ashdod Site operational times 


In his proposal the Contractor shall submit the cost of Service and Maintenance for each of the following options:

7.5.3.1 Standard operational hours of the facility:

a. 07:00 – 22:30 (2 shifts).
b. 5 days/week.
7.5.3.2 Option 1 - operational hours:

a. 24 hours (3 shifts).
b. 5 days/week.
7.5.3.3 Option 2 - operational hours:

a. 07:00 - 17:00 (1 shifts)

b. 5 days/week
7.5.4 On Site Technician

7.5.4.1  As long as the service and maintenance agreement is in force, the Contractor shall provide a full-time contractor’s employee positioned on the site at site's working hours to perform the works.

7.5.4.2 Services of the aforesaid maintenance employee will be given in the framework of the system maintenance at no additional cost.

7.5.5 Please note that the on site Contractor's maintenance employee has to start and prepare the facility before a site operation begins (at 07:00) and that an overlap of an hour between the shifts is required. 

7.5.6 The Client reserves the right to order from the Contractor at the end of the warranty period the supply of service and maintenance to be provided by the Contractor in accordance with the following provisions for the initial term.

7.5.7 The service and maintenance agreement will be automatically renewed at the end of each term for another term, during the period of the said 10 years, unless the Client decides not to renew the agreement and gives written notice to the Contractor at least 60 days prior to the end of the agreement term.

7.5.8 Upon receipt of the Client notice that the Client has decided not to renew the service and maintenance agreement, the Contractor will initiate the preparation of appropriate training materials, and will train technicians designated by the Client for the implementation of the service and maintenance.

Training will be for 2 weeks on-site in Israel at no cost to Client. The Client will be responsible for the cost of additional training days beyond the 2 weeks if requested by the Client.

7.5.9 For the purpose of providing maintenance and service, the Contractor undertakes to retain sufficient supply of spare parts for at least 10 years from the last date of successful completion of the final acceptance test.

7.5.10 The Contractor shall maintain in Israel a sufficient supply of spare parts to enable him provide service within the response times set forth below.

7.5.11 As long as the service and maintenance agreement is in force, the Contractor undertakes to repair or replace any equipment or parts found to be defective, faulty or inoperable during the use of the system, equipment and/or spare parts.  In the event that a faulty or defective part is repaired by the Contractor three times during one year he shall be obligated to replace it with a new one and in all systems and shall not be permitted to repair it again. 

7.5.12 Repair and/or replacement for the purposes of this paragraph shall mean:

a. Locating the breakdown

b. Obtaining the supervisor’s approval for a change in equipment /system

c. Transportation

d. Installation, connection or replacement of components

e.  Technical changes or adjustments

f.  Testing 

g. Any other operation required to return the system to proper operation and to bring it up to the standard operational status required under the specifications stated by the contractor. 

7.5.13 The repair shall be performed on the site where the defective part is operated, installed, or stored. 

7.5.14 The Contractor shall bear all costs involved in executing the repair and/or the replacement in the format set forth above, including costs of travel and security for the service personnel, to the extent required, due to the security situation on the sites where the system is installed, or on the roads leading thereto. 

7.5.15 Comprehensive preventive maintenance

7.5.15.1 The Contractor shall detail in his proposal the maintenance plan referring to the following:
· Maintenance type:

· Daily

· Weekly

· Monthly

· Half year.
·  Works content (what and how) for each works type

· Performing body

· Works duration.
7.5.15.2 In addition to the routine service and maintenance comprising of tests and works performed at a frequency and quality as required by the level of operation of the system (duty cycle) and environmental conditions the Contractor shall perform comprehensive periodic preventive maintenance each six (6) months. 
7.5.16 Periodic Performance Tests

7.5.16.1 Each year, following the comprehensive periodic maintenance works Verification Tests of the radiographic system performance will be performed. 
7.5.16.2 The objective of the tests is to verify the compliance of system performance with the performance as was determined during system's final acceptance tests (at least the mandatory minimum).
7.5.16.3 The protocol of these tests is identical to the protocol of the final acceptance tests, using the definitions and means as defined in Section 5. 
7.5.16.4  Tests results will be submitted to the Client as part of the signed report.  

7.5.17 Reports - The Contractor is required to submit a report for each repair and periodic tests he makes.  The report shall include: 

p. The name of the person from the facility who reported the malfunction. 

q. Call time, time of arrival on-site, service completion time. 

r. Description of breakdown.

s. Description of repair or periodic test made. 

t. Details of components, assemblies, units replaced or repaired. 

u. Each report shall be made in 4 copies:  Customer (Person in Charge of the Installation); Contractor; Machine log book at the site; Machine log book at the service firm. 
v. The reports shall be routinely mailed to Site's Manager and to the Manager of Customs Technologies  
w. Each report shall be signed by a representative of the Customer and the Contractor;

x. Everything contained in the reports shall be fed into and maintained in a computerized database, on the Contractor’s responsibility, under electronic systems and components management and maintenance programs. 

y. The Contractor shall provide, monthly and at the Customer’s request, statistical breakdown analysis with varied and various cross-sections and particularly with an item description cross-section according to catalog number and serial number, with an analysis of the history of the breakdowns of this item/sub-system. 

7.5.18 In each case of malfunction or incompatibility of the system, the Contractor shall take immediate action upon receiving notice from the Client to remedy the malfunction and to bring the system to a working and operational capability.

7.5.19 The Contractor undertakes to comply with the response times set forth below: 

z. Minor breakdown - a breakdown that does not result in a general halt in the system’s operation, and does not adversely affect any required performance. 

aa. Complete halt - a breakdown that causes a complete stoppage of the system or obligates it to cease operating since the system’s performance has been adversely affected. 

ab. Required repair times:

Minor breakdown - less than 24 hours. 

Complete halt - less than12 hours.
 
The Contractor undertakes, within this period of time, to return the defective system to full operational status, including the carrying out of any necessary repairs. 
7.5.20 Breakdowns deriving from “Act of God” or sabotage
 
Breakdowns during the warranty period or during the period the service and maintenance agreement is in force, deriving from “force majeure” or malicious damage shall be repaired by the Contractor as required by the contract/order, however the payment for work hours, spare parts and assemblies supplied in this case shall be paid by the Client in accordance with the prices in the original proposal. 

7.5.21 The conditions for each year of the service and maintenance contract under the above terms shall be set forth in the proposal.

7.6 Reliability and Availability

7.6.1 Radiographic System availability will be 95%.

7.6.2 The normal duty cycle of the system will be: 16 hours/day, 5 days a week 52 weeks a year. 
7.6.3 If required the Client shall operate the system at nights or during weekends – this with no additional cost or any warranty restrictions.  
7.6.4 System Mean Time between Failures should be minimal in order to provide high reliability. The Contractor must include in the proposal statistical data of the proposed system MTBF.
7.7 Update /Upgrade

7.7.1 As part of the Service and Maintenance long term contract an update of main systems, especially of the computer and the radiography system will be provided.

7.7.2 The first Update will be implemented not later than two (2) years after the end of Warranty year. The second update/upgrade will be executed not later than three (3) after the first update, and the third update/upgrade will be executed not later than three (3) after the second one.
7.7.3 The update will include software update as well as radiography system hardware upgrade.

7.7.4 The Contractor will submit a detailed plan for the proposed upgrade in his proposal.

7.8 Spare Parts 

7.8.1 The Contractor shall supply, as an integral part of the service and maintenance agreement, a 7-year (not including the warranty period), supply of those spare parts needed as a result of normal wear and tear, at no additional cost.

7.8.2 Wherever in the system there is a fuse the Contractor shall supply 5 such fuses, which shall be placed in a specially padded container in or close to the equipment with a special sign indicating appropriate designation of the container. 

7.8.3 The minimum level of spare parts as well as necessary components within the assemblies maintained by the Contractor shall be adequate to effect immediate repairs. 

7.9 Contractor Cost proposal

7.9.1 The Contractor shall submit a price commitment for these services with the proposal, including:

7.9.1.1 The price for each additional year of the 10 years of extended warranty

7.9.1.2 The price for radiography system updates every three (3) years (hardware and software, including training software)
8. Design Guidelines and Data

8.1 General

8.1.1 The significance of the guidelines


The general guidelines and data appearing below form together with the terms the scope of work in this project. 


All the documents are mandatory even though some instructions may appear to be a recommendation. 

8.1.2 These guidelines refer to:

a. Complete and detailed planning of the radiography systems, conveyor systems, electrical installations, air-conditioning, fire detection and extinguishing systems, etc., as specified, based on a specification including full engineering coordination between all the electromechanical systems.

b. Complete and detailed planning of items of equipment that the contractor shall supply and their installation in the various buildings. 
c.  Any work and/or installation required for the acceptance of the site and any other work required according to this document for the complete and full acceptance as a turnkey method.

8.1.3 The scope of the guidelines


As stated above, the guidelines and data in this part are general and are intended to define the general requirements for the planning and performance of all buildings/facilities/systems and works within the Scope of Work. The detailed guidelines, data and requirements for the planning and implementation which are reflected in the special specifications of the various work chapters, drawings and other documents of the SOW complement each other together form the complete design requirement for the acceptance of all the buildings, their systems and other works described in a complete manner and ready for operation.

8.2 Mandatory applicable standards, specifications and data

8.2.1 The work shall be designed and carried out according to Israeli laws, regulations and standards. In the event that such standards do not exist, applicable American, or EU standards may be used. All the standards used shall be in the latest edition, updated to the date of submitting the proposal.

8.2.2 The applicable mandatory standards and specification for the design and implementation of this work are according to the following order of priorities:

a. Israeli laws, regulations and standards.

b. US standards and specifications.  
c. European standards and specifications.

8.2.3 The Israeli laws, regulations and standards are as follows:

a. Planning and Construction Regulations.

b. Electrical Codes and Israel Electricity Law (IEL).

c. Safety Regulations.

d. Work Safety Regulations (Industrial medicine and health of ionizing radiation workers).

e. The Inter-ministerial General Specification for construction work (Issued by the Ministry of Defense, latest edition).

f. Israeli standards issued by the Standards Institution of Israel.

g. Fire Fighting Authority Regulations.

h. IDF Regulations for shelters and Civil defense. 

i. Sanitary installation instructions.

j. Work Inspectors' Organization Regulations (environmental and biological monitoring of personnel working with dangerous materials).

k.  Communication Standards Regulations
l. Environmental Hazard Prevention Regulations.

m. Earthquake resistance planning should be according to standard.

8.3 ISO Standards

8.3.1 The required systems shall comply with international recommendations and standards such as ISO standards or equivalent and with the conditions envisaged in this specification. Instruments manufactured to standards other than international ones will not be considered.

8.3.2 The contractor shall submit all the necessary certifications confirming compliance with ISO quality control standards or equivalent. 

8.3.3 The above certifications are required for the component level, production and assembly, and for the system level. 

8.3.4 The above certifications are required for the maintenance firm as well.

8.4 Substitution of Materials or Products

8.4.1 Should the Contractor request to substitute a material or product (specified or approved), details of the material or product shall be submitted to the CR. The representative will consider approval, if the following conditions are fulfilled:

8.4.1.1 The new material or product is equivalent or superior in quality to the original.

8.4.1.2 The substitution of the material or product shall not constitute grounds for a claim by Contractor for additional payment, even if the new material or product is of superior quality.

8.4.1.3 If the price of the material is cheaper, the Contractor shall cut his price.


The Client's representative does not undertake to approve such substitutions (even if the above conditions apply).
8.5 General Guidelines 
8.5.1 Guidelines for site development

8.5.1.1 General


The earthworks, site development works and paving works will be based on the planning data, soil reports and the planning implications of the equipment and vehicles provided by the contractor, and additional specific vehicles allocated for this project by the Client for fulfilling occasional tasks.

a.
The planning serves as basic guidelines for the detailed design that the contractor shall submit. The quantity of parking spaces and sidewalks is a minimal requirement.

b.
The widths of roads, sidewalks and concrete platforms are minimal requirements. The contractor design will be based on full size trucks and/or platforms suitable for carrying 20-ft and 40-ft containers.

c.
Turning radii will be determined according to accepted design criteria and, in any case, will enable standard and long vehicles, such as trucks, to make the turns.
8.5.2 Electrical & electromechanical systems

The electrical & electromechanical systems shall meet the following standards:

a.
The latest version of the Israeli Electricity Law, 1954.

b.
The latest edition of the Inter-ministerial General Specification No. 08 of MOD and the Standards mentioned there. 

c.
The MOD Construction Center Standards.

8.5.3 Communication systems   

8.5.3.1 Infrastructures for the communication system were implemented at the site according to communication standards and specifications of:
a.
Bezeq Ltd.- Israeli Telephone Company.

b.
The Standards Institution of Israel.

c.  
ISO/IEC - International Electro-technical Commission.

8.5.3.2 It's contractor's responsibility to check whether the existing communication infrastructure matches contractor systems requirements and connect appropriately (interface).
8.5.4 Air-conditioning system

8.5.4.1 The planning requirements are described in Section 6 (Air-Conditioning Chapter).

a.
The contractor shall prepare thermal calculations for each room according to the calculation method of ASHRAE Guide.

b.
The weather calculations are based on the following outdoor conditions:

	
	Summer
	Winter

	Dry bulb temperature
	38(C
	5(C

	Wet bulb temperature
	24(C?
	3(C


c.
The heat loads of the indoor equipment depend on the equipment supplied.

d.
Indoor conditions

 
Control center building


Air-conditioned offices:  
22(1(C


Air-conditioned X-ray 

 
Equipment and control rooms: 
22(1(C, 50% RH ((5%).


Air-conditioned UPS room:
22((2(C.

8.5.4.2 As part of this project the air condition system in the Radiography building shall be replaced.
8.5.5 Sanitation system
8.5.5.1 The sanitation systems shall be designed according to the following Standards and Specifications:

Sanitary Systems Instructions, (HALAT) 1980

Inter-ministerial General Specification, Chapter 07 & 57, 1990

Israeli Standards 1205 & 1285 & 884

8.5.5.2 The system planning shall include, among others, the following elements:

a.
Water supply, sewer and draining of sanitary facilities inside the buildings.

b.
Water supply to air-conditioning systems at the required locations and draining condensate from the air conditioning systems.

c.
Installing hydrants and fire fighting stations, in and outside the buildings, as stated in the Special Specification as well as a water supply to all hydrants and hose rollers.

d.
Automatic water extinguishing systems.

e.
Supply of water to water cooling facilities.

f.
Outdoor sewer lines and city water lines and connections to existing systems.

g.
Draining rainwater from building roofs.

h.
Water supply and piping system for irrigation.

8.5.6 Safety systems guidelines


Fire detection and fire-fighting systems shall be designed as required in this document.

8.6 Acoustic requirements

8.6.1 The contractor shall plan and implement the building according to the following principal acoustic guidelines:

a. If necessary, silencers will be installed in the openings of the building envelope and the entrance doors will be acoustic.
b. The acoustic insulation of the plasterboard partitions of the offices and the control rooms shall be at least 45 dB.

8.6.2 All buildings, openings, human engineering, presentation systems and equipment installed at the site shall be planned, built and installed according to Israeli human engineering instructions as defined in the Israeli standards. (MIL-STD-1472 of the latest edition)
8.7 Electro Magnetic Compatibility (EMC)
8.7.1 All buildings, systems and equipment installed at the site shall be planned, built and installed so that they shall not affect or be affected by other systems which have EMI and RFI effects
8.7.2 In case Bidder's implementation requires additional Transformation system, the equipment shall not be installed inside office building.

8.8 Environmental Data for Planning

8.8.1 The installation shall operate under Israeli climatic conditions. 

8.8.2 In designing the installation, the following environmental conditions should be taken into account.
	Temperature
	Minimum of 00 C – maximum of 500 C

	Humidity
	The proximity of the installation to the sea (10%-98%)

	Rain
	

	Hail
	

	Solar radiation
	

	Sand and dust
	Resistant - The area in which the installation is located

	Saline Atmosphere
	The proximity of the installation to the sea.

	Wind
	The area of the installation is exposed

	Fungi
	

	Lightning
	

	Water Sprinkling
	Washing the equipment and cleaning the site

	Immersion
	Of equipment, especially the mechanical system


8.8.3 Special attention must be paid to deal with thunderstorms and all necessary equipment shall be installed to prevent the damages caused by hit of lightning. 
8.8.4 The installation will function in the defined environmental conditions without any reduction in the performance of systems or equipment as defined in this SOW. 

8.8.5 The contractor will be obliged to supply a declaration confirming compliance of the system with Israeli law, regulations and requirements as set down  by the Israeli Ministry of Environmental Protection.

8.9 Requirements for Software Design

a. 
The software shall be developed in accordance with the Israeli Standard for Software 2000.3 (compatible with the ISO-9000-3 Standard) and with international standards.

b.  
In the PDR, the contractor shall define the software requirements which will be developed and installed in the systems described in this SOW.

c. 
The software and Hardware should be ready made for the most relevant and up to date version.

d.  
Surveys will be conducted in respect of the software in accordance with the surveys specified in this SOW. 

Appendix A

Guidelines for technical proposal
1. General
1.1 The Contractor shall submit his Proposal in 7 copies (five hardcopy and two digital media), in English

1.2 The Contractor shall list the designer and consultant teams that the Contractor intends to employ for planning and overall supervision. All the designers must be duly registered and licensed according to their field of expertise.

1.3 The Contractor shall specify how the project will be managed and executed in Israel, including the details of the executing engineer to be employed by the Contractor and the major subcontractors chosen.

1.4 The Contractor shall indicate in his proposal how he plans to meet the schedule for concluding the work on time, and prepare detailed monthly schedule (GANTT diagrams) containing project milestones.

2. Technical Documentation

2.1 The Contractor will attach the following documents about the systems:

· Systems description (Radiography, Traffic control, Safety, Security, etc.)
· Operator manuals

· Maintenance plan and documentation for each level required, including:
a. Periodical (daily, weekly, monthly, yearly) maintenance, performing body, required time, schedule and detailed content of the works
b. System maintenance manual, preventive maintenance
c. Detailed plan for the periodical (3 years) upgrades.
2.2 The Contractor will specify the current compliance level for each of the above, in terms of complying with the requirements detailed in this document. Rate as follows:

(
Fully ready - All documents are as specified.

(
Partially ready - We can complete the requirements by the RFP specified schedule.

(
Not ready - We do not have the documentation for the required level, and it should take X months to finish it.

3. Contractor's Experience

3.1  The Bidder shall submit detailed description regarding his experience in similar projects and including:
a) List of implemented projects (type, date, location, etc) 

b) List of implemented projects he upgraded

c) List of customers/point of contact

d) Short description of each project

e) Project delivery date

f) Duration of upgrading project implementation (from contract date to delivery)

g) Client's certificate in support of the satisfactory implementation of an upgrade project as well as of a satisfactory operation of the system supplied by the Bidder
h) Detailed analysis regarding minor/major faults and system downtimes in previously implemented systems;

i)  Detailed analysis of weather conditions, including extreme weather conditions, valid in sites the system was implemented.
3.2 List and description of all subcontractors.
4. System description

4.1 Detailed proposed systems description will be submitted by the Contractor, including:

a. General description.
b. Operational description of the whole process on the Site.
c. List of all sub-systems/data sheet of equipments and furniture, including details regarding:

· Manufacture/supplier

· Type/Model

d. Technical specifications of all subsystems, including Radiography system, Conveyor / Scanning system, Image workstations, Computer and control systems, Command and Control systems, etc.

e. Radiography Systems performance, for the New and the Intermediate system (in the defined 9 positions), in reference to all parameters, as defined in section 5, including:

· Throughput

· Ultimate Penetration

· Wire IQI

· Hole IQI

· Additional system capabilities; for example Material discrimination 

· Shielding required to reduce radiation zone (for the New and the Intermediate x-ray systems)

· Radiation Dose Rate and Maximal Radiation Level, for the following:

· Absorbed per Inspection 

· 
In operator rooms 

· Visitors 

· Environment

f. Personnel required for systems operation:

· Minimal - to achieve the required throughput

· Recommended

g. Quality Assurance
5. Service and Maintenance
5.1 Detailed description will be submitted, including:

1) Location of Service center in Israel;

2) Name and experience of the Service Company;

3) List of test equipment;

4) List of Company Manpower;

5) List of spare parts, hold in Israel by the Service Company.

6) Maintenance plan, specifying for each subsystem the following:

· Maintenance content

· Period

7) Compliance with required regulations and standard

8) Contractor's Commitment for Service supply for at least 10 years.
6. Compliance table

6.1 Requirements Fulfillment Statement

6.1.1 The Contractor shall declare, in writing, that the proposed system (as a whole and as individual components) will fulfill all of the specified requirements listed in this SOW document.

6.1.2 In addition to the declaration above, the Contractor must specify and refer to each of the applicable documentation paragraphs its specific solution. Meaning, for each paragraph of this document, the Contractor must specify if it complies with the specification and how the solution fits to the specification detailed in the paragraph. 
This must be built as a compliance table such as the following example:
	Paragraph No.
	The specification details
	Fulfillment level
	Notes

	X.Y.Z
	Penetration
	Fully
	The system was designed to reply to this specification while using advanced detectors as shown in section xx.yy.zz in the Proposal.

	…
	…
	…
	…


The Contractor should refer to each of the proposed buildings, facilities, and operational systems, etc.

	Section
	Chapter & Paragraph
	Description of Paragraph
	Contractor compliance
	Equipment

	6G
	1.1
	CCTV cameras
	+
	XXXX Model 111


Appendix B - Price Proposal
	No.
	Subject
	Project Contents
	Options

	
	
	Remarks
	Price (IS)
	Subject
	Price (IS)
	Subject
	Price (IS)

	1
	Dual-view Radiography system
	 
	 
	 
	 
	 
	 

	1.1
	Radiography System
	
	
	
	
	
	
	

	1.2
	Additional IAW
	 
	 
	 
	1
	 
	 
	 

	1.3
	New Shielding doors 
	 
	        
	 
	 
	 
	 
	 

	1.4
	Shielding Doors – renewed 
	
	
	
	2
	
	
	

	2
	Scanning subsystem
	 
	 
	 
	 
	 
	 
	 

	3
	Intermediate screening system
	 
	 
	 
	 
	 
	 

	4
	Control subsystems
	 
	 
	 
	 
	 
	 
	 

	4.1
	Traffic Control System
	 
	 
	 
	 
	 
	 
	 

	4.2
	Security Systems
	 
	 
	 
	 
	 
	 
	 

	 
	 
	 
	 
	 
	 
	 
	 
	 

	5
	Civil Works
	 
	 
	 
	 
	 
	 
	 

	6 
	Stand-alone software for Image Analyzers training 
	 
	       1
	 
	
	 
	 
	 

	 
	Total
	 
	 
	 
	 
	 
	 
	 

	6
	Service & Maintenance 
	
	 
	 
	option 1 (3 shifts)
	 
	option 2 (1 shift)
	 

	 
	 
	1st year
	 
	 
	 
	 
	 
	 

	 
	 
	2nd year
	inc. update
	 
	 
	 
	 
	 

	 
	 
	3rd year
	
	 
	 
	 
	 
	 

	 
	 
	4th year
	 
	 
	 
	 
	 
	 

	 
	 
	5th year
	inc. update
	 
	 
	 
	 
	 

	 
	 
	6th year
	
	 
	 
	 
	 
	 

	 
	 
	7th year
	 
	 
	 
	 
	 
	 

	
	
	8th year
	
	
	
	
	
	

	
	
	9th year
	
	
	
	
	
	

	
	
	10th year
	
	
	
	
	
	

	 
	Total
	 
	 
	 
	 
	 
	 
	 


Section 2.doc 
2-1
48
Section 2.doc
2-77 


