27

SECTION 6 - SUB-SECTION G

SPECIFICATIONS OF THE FCS (FACILITY CONTROL SYSTEMS)

CONTENTS

1.
General
6G-2

2.
Purposes of the Control Systems
6G-3
3.
Facility Control System (FCS)
6G-4
4.
Radiation Control System (RCS)
6G-4

5.
Shipment Directing and Monitoring System (SDMS)
6G-5
6.
Security and CCTV systems
6G-15
7.
Technical Requirements
6G-20
1. General

1.1 The facility in its entirety includes various systems, each working separately at a different level of automation and including various backup possibilities.
The availability and reliability of the systems constitute an indispensable condition for the proper and continuous working of the designated equipment installed in the facility.

1.2 The various control systems will give an up-to-date real-time status report of site's systems and vehicle traffic and will caution regarding deviations from routine. The control will operate backup systems and will allow coping with emergency situations (radiation, fire, etc.).

1.3 Command and control of the site will be provided mainly by the following Three (3) main systems, each fulfilling a different function:

1.3.1 Shipment Directing and Monitoring System (SDMS) - Traffic Control System (TCS)
1.3.2 Radiography Control System (RCS)

1.3.3 Security Systems: Perimeter and site security
1.4 Each one of these systems should function as a stand- alone systems, the first two control systems (SDMS and RCS) comprise the FCS.

1.5 The Contractor shall present systems' configuration at the various locations/positions as required at the DR meetings. 

1.6 Acceptance tests protocol for each system shall be presented by the Contractor for Client's approval.

1.7 The subcontractor for the Security and SDMS systems and subsystems shall be an Israeli integrations company with proven service and maintenance capabilities.
1.8 The Contractor is responsible for the implementation, testing and training as well as the service and maintenance of these systems. 

1.9 Thunderstorm / Lightning Protection 

1.9.1 All supplied equipment will be lightning and surge protected.

1.9.2 The protection will comprise: power sources, electrical sockets, data lines etc.
1.10 All supplied equipment, designed for outdoor and indoor installation, shall comply with the weather and environmental condition as specified in Section 2 (Clause 8.5) and its operation will not be affected by environmental conditions.
1.11 Contractor's proposal shall include a detailed description systems configuration and technical specification, including these regarding computers and servers. Final configurations and systems specifications shall be defined and approved at the DR meetings.

2. Purposes of the Site Control Systems

2.1 The purpose of the Command and Control of facility systems is:

2.1.1 To ensure and control site safety

2.1.2 To control vehicle traffic at all stages of the work at the site

2.1.3 To control and efficiently operate the X-ray inspection installation and the manual site
2.1.4 To ensure and control site security 

2.2 To present at required workstations the relevant data regarding cargo contents and to provide maximum information and instructions defining the inspection required.

2.3 To efficiently cope with emergency situations and deviations from the routine by appropriate warnings or/and intelligent operation of backup units, either by automatic or by manual operation
2.4 The system will make it possible to locate faults and repair them within pre defined periods of time. 

2.5 To serve as a tool of control access to the facility/buildings or rooms and to integrate into the overall safety and security systems of the facility;
2.6 To provide an up-to-date status report on the status of all the systems to relevant agencies in the facility.

2.7 To serve as a tool for centralizing of cumulative information, trends and characteristics of the systems in the building, for purposes of analysis of behavior, drawing of conclusions and raising the level of performances and reliability of the system on the basis of "historic" information and locating of failures.

2.8 To serve as an objective and reliable tool for analysis of failures, their causes and characteristics, as a basis for the engineering analysis of the faults and an attempt to prevent them in the future by changing of parameters or drawing of operational conclusions.

2.9 To serve as an engineering aid for support of the system operation and maintenance;
3. Facility Control System (FCS)

3.1 The Facility Control system comprises of: 

3.1.1 Radiographic control system (RCS) 

3.1.2 Shipment Directing and Monitoring system (SDMS) including the Traffic Control System (TCS) 


Thus, the FCS controls all the operational processes taking place at the site.

4. Radiation control system (RCS)

4.1 The RCS deals at the command and control level with the following elements:

4.1.1 Movement of the trucks on the conveyor in the radiation tunnel.

4.1.2 Operation of all the safety means of the radiation system

4.1.3 Operation of the X-ray inspection system.

4.1.4 Suspension of X-ray on conclusion of the scanning process.

4.1.5 X – Ray Image acquisition, analyzing process and Image Data base updating.

4.2 The X-ray inspection control system shall work in functional integration with the traffic control system (SDMS). In addition data transfer from RCS to the SDMS will be provided.

4.3 The system software shall include all the routines required for sustaining the conditions and proper operation as regards of operation and safety.

4.4 The system will contain appropriate backups for operational compliance with very high safety requirements.

4.5 The control terminals of the RCS will be installed at the following positions:

4.5.1 X-ray inspection system operator position – fully operational.  

4.5.2 Shift supervisor position – display only: status and graphic.

4.6 At the PDR the Contractor will present, for Client approval, all aspects of control system's operation. 
5. Shipment Directing and Monitoring System (SDMS)

5.1 General

5.1.1 The SDMS will be designed to intake incoming shipments, identify the trucks using ALPR and in combination with driver's identification tag to control and route the movement of vehicles in the site area and the access of pedestrians as specified.

5.1.2 The SDMS shall be designed to efficiently control the procedures described in section 3 of this document.

5.1.3 The control systems have the following main tasks:

5.1.3.1 SDMS - Direct and control movement of container/cargo trucks at entry, at all stages of the activity on-site and at exit gate. Control shall be provided with resolution of a single vehicle.

5.1.3.2 Access Control of people in facility areas
5.1.3.3 Managerial control, providing data to correlate with customs data. 
5.2 Purpose of the system

5.2.1 Routing and directing the vehicles.

5.2.1.1 The system will include identification and directing means as specified below:

a. Truck ID – based on truck front License Plate Number (TR)

b. Container ID – based on Container unique serial Number (ISO6346)  (CC)

c. Identification tags to be given to the drivers (Inspection/Driver ID)

d. Identification tag reading units to be installed on the site

e. Directing signs, traffic lights, Barriers and more.
This, in order to allow routing, command and control of all the traffic in the site and throughout the process, from the arrival of the vehicle at the facility gate until its departure.

5.2.1.2 The system will implement directing means as specified below:

a. Dynamic signposts which variable messages according to the directing needs.

b. Traffic lights 
c. Barriers and gates
5.2.2 Correlation with Customs data 

5.2.2.1 Purpose of the system:

a. To display the data of the cargo/container's contents at the relevant work stations.

b. To indicate special inspection requirements for the shipment.

c. To define the type of the required inspection (R / M / R+M)

5.2.2.2 Cargo data is acquired from the following sources:

a. From customs computer – throughout the unique Inspection Number, defined at the check-in
b. The document scanner.

c. Manual entry.

5.2.2.3 The contents of the data shall include the relevant information for implementation of the designated inspection: X-ray or/and manual process 

5.2.2.4 It shall be possible to present the screen containing the cargo data at the relevant workstations deployed in the facility (as specified in Sections 3 and 4)
5.2.2.5 The contractor will take into account the need to attribute space in furnishing of the positions in which system equipment will be installed.

5.3 Components of the SDMS and subsystems
5.3.1 The control system shall include the following components:

5.3.1.1 Access Control subsystem

5.3.1.2 Identification tags – employees and truck drivers.
5.3.1.3 Readers – LPR, Container unique serial number, ID cards
5.3.1.4 Electronic Signs & Traffic lights
5.3.1.5 Computer system for management and communication.

5.3.1.6 Auxiliary equipment (cables, kits etc.)
5.4 Access Control subsystem - People
5.4.1 Current Status

5.4.1.1 Currently the access control system in the site is based on employees' ID cards. 
5.4.1.2 The system is deployed at entrance to some rooms, mainly sensitive sites as regards of security, safety and/or operational functioning.

5.4.1.3 The system is based on Card readers installed close/at the controlled doors/gates.
5.4.2 Requirements

5.4.2.1 The Contractor shall install Client's approved Access control system at pedestrians' entrance near the main entrance gate from external road (G).

5.4.2.2 System's software package regarding access control and including all the standard functions, for instance: restriction of entry times, restriction of entry sites, prevention of possibility of reentry, etc. shall be installed at the gate wicket.
5.4.2.3 Access control activity shall not disrupt the operational activity of the traffic routing system.
5.4.2.4 The contractor will install / replace the existing access control equipment at the following locations: 

· The entrance to the radiography building (D)
· The entrance to inspectors room from the manual search area
5.5 Readers

5.5.1 General

5.5.1.1 Readers, part of SDMS system, shall be installed in the following locations.

a. Main Gate (G) – entry/exit lanes
· Pedestrian entrance - Employee card reader

· LPR – Entry lane for private vehicles

· LPR – Exit lanes for exiting trucks and private vehicles

· Driver's Tag reader – truck exit lanes (backup)
b. Check-in area (A) - 2 entrance cabins

· LPR – acquire the LPN of check-in trucks at two lanes. 

· OCR – acquire the Container code number at two lanes
c. X-ray inspection building (D)
· LPR - Entrance to X-ray inspection tunnel
· OCR -  Container unique serial number
· Driver's Tag reader – receptionist/operator's workstation

· Entrance doors to control room, offices and classified rooms (total of 10) - Employee card reader.

d. Manual inspection installation (E)
· Driver’s tag reader  - At inspector's office (recheck workstation)
· Driver’s tag reader  - At the inspection pit
· OCR -  Container code number
5.5.1.2 The readers shall be installed in places which will not affect movement of the vehicles.

5.5.1.3 The reader equipment shall be designed for outdoor installation and their operation will not be affected by environmental conditions.

5.5.1.4 The readers will be installed with a level of resolution allowing continuity of command, supervision and control in all areas of the site.

5.5.1.5 The readers of identification tags, either Driver's tag or employee's ID card, direct access of the card holder is required.
5.5.1.6 The readers for identification of vehicles (ALPR) will be able to read the front license plate number of a moving vehicle (position indifferent)
5.5.2 Card Reader (access control)

5.5.2.1 The card reader will meet the following requirements:

5.5.2.1.1 There will be indicator lights at the entrance showing “Authorized” or “Rejected”.

5.5.2.1.2 A buzzer will sound to give an audible indication for “Rejected”.

5.5.2.1.3 The lifespan of a reader should be at least 2,000,000 movements.

5.5.2.1.4 Minimum working temperature range 0°C - +50°C.

5.5.2.1.5 In the event of a failure in communication or in the system server, the card readers must work completely autonomously (using a local controller), and without any interruption to the entry and control of users.  When the communication returns to a normal state, the system tables shall be updated immediately.

5.5.2.1.6 The reader will work using power supplied by the buildings controller.

5.5.2.1.7 The readers shall be protected by a tamper proof switch so that disassembly of the reader will cause an alarm in the system.

5.5.2.2 Every reader/controller shall transmit indications to the system server as follows:

5.5.2.2.1 Authorized gate entry.

5.5.2.2.2 Manual gate entry (by the internal button).

5.5.2.2.3 Attempt to disassemble the reader/server.

5.5.2.2.4 Communication error.

5.5.2.3 Readers designated for multi-use will include function buttons and an alpha numeric keypad.

5.5.2.4 Mechanical characteristics.

5.5.2.4.1 The fitting of the card readers within the facility will be of the anti-vandal indoor type, suitable for the environmental conditions within the building.  Installation of a reader outside the building will be within outdoor weather-proof anti-vandal fittings and must meet both UL-294 and CE standards.

5.5.3 Truck Driver's ID Tag
5.5.3.1 Driver tag, given as part of the check-in procedure, will be made of rigid paper, locally obtainable. 

5.5.3.2 The tag will contain the following information:

a. Inspection/Truck ID (unique inspection number) - human and machine readable

b. Date/Time

c. Truck next destination

d. Designated parking lane number

e. Container unique serial number
5.5.3.3 Driver identification tag will be a bar code (or similar) type.

5.5.3.4 The identification tags will be prepared at the check-in workstation after acceptance of the shipment has been authorized. The tags shall be for one-time use and unique for each shipment/inspection.

5.5.3.5 Functioning of the tags shall not be affected by weather conditions (rain, wind, etc)
5.5.3.6 When the truck exits the site, the identification tag will be (preferably) swallowed at the exit gate or put in a special device. 

5.5.4 Licence Plate Recognition (LPR / ALPR)

5.5.4.1 General


Monitoring container traffic into/at and out of the site is based on identifying trucks license plate number at the required locations.

5.5.4.2 Operation

5.5.4.2.1 The system shall acquire and recognize license plate number of private cars and trucks. 

5.5.4.2.2 The LPR system will be installed at the following locations:

· Two Entrance and Exit lanes at area G

· Two Entrance lanes at check-in area A

· Entrance to the radiation tunnel - D 
5.5.4.2.3 Private cars - The system will recognize car license plate and will compare it against files of authorized and unauthorized vehicles.

5.5.4.2.4 Reading of the vehicle's license plate shall be of the vehicle's front license plate. 

5.5.4.2.5 It should be noted that location of truck's license plate varies from one truck to other and may be located at the front of driver cabin.
5.5.4.2.6 Each lane will include two (2) IR cameras with IR illuminators.

5.5.4.2.7 The system shall acquire more than one image to insure reliable reading of car license plate.

5.5.4.2.8 Dedicated software shall be supplied with the system.

5.5.4.2.9 Response time of vehicle's license plate recognition will not exceed 3 second.

5.5.4.2.10 Detection wire loop in the asphalt (to supply trigger for camera operation) is required.
5.5.4.2.11 Technical requirements:

· Road width: 4 meter.

· Operation distance: up to 15 meter from the vehicle.

· Vehicle speed: 0-80 km/h.

· The system will have al least 4 dry contacts for external equipment operation.

5.5.5 Electronic signs 

5.5.5.1 The electronic Sign, LED variable message sign displays shall be installed in the following locations:

5.5.5.1.1 At the pre-radiography Parking Lot
5.5.5.1.2 At the pre-clearance parking lot (post radiography)

5.5.5.1.3 At the Manual site (E) 
5.5.5.1.3.1 Inspection area, near inspectors room

5.5.5.1.3.2 Drivers waiting room (smaller one)
5.5.5.2 The outdoor sign shall be sunlight readable, large characters and the viewing angle adjusted so that they can be clearly visible to all drivers.

5.5.5.3 Technical Specifications:
5.5.5.3.1 Display Type: HRSBSC3280, Hi Res. Sun Blazer.

5.5.5.3.2 LED's per Pixel: 1.
5.5.5.3.3 Color: Amber.
5.5.5.3.4 Pixel Matrix (H x W): 32 X 80.

5.5.5.3.5 Pixel Size: 0.51 cm.
5.5.5.3.6 Pixel Pitch: 2.29 cm
5.5.5.3.7 Active Display Area: 73.1 cm X 182.8 cm (approx.).
5.6 SDMS Computer system 
5.6.1 Requirements
5.6.1.1 The system software will be user-friendly and will allow rapid access to every function.

5.6.1.2 It's preferred that the user interface display will be in Hebrew. 

5.6.1.3 Access to the system functions will be by authorization (password).
5.6.1.4 The system will be able to alert on mistakes/errors in reading identification tags.

5.6.1.5 Communications with other computers will be rapid and will not affect operation of the system in the various work modes.

5.6.1.6 The system will alert on attempts at unauthorized tampering and/or handling of card readers.

5.6.1.7 The system will be planned with a capability for 100% expansion.

5.6.1.8 The system will operate in integration with other systems
5.6.2 SDMS display
5.6.2.1 The SDMS is a tool to manage, monitor and control vehicles in the facility. 
5.6.2.2 The system software has to meet all the above requirements.

5.6.2.3 The interactive map shall display the lists of trucks currently located at site's areas, for example: pre-radiography parking, the radiography tunnel, pre-clearance parking, manual area, pit, exit cabin. The list shall be created based on the recorded outputs of the SDMS detectors/equipment located at the various areas and system's interface with the radiography software. 
5.6.2.4 At the SDMS design Review, the Contractor shall present, for Client's approval, the proposed configuration and specific parameters of the SDMS display, including reference to the following:
5.6.2.4.1  Status of each truck in the site - shown dynamically on site map background
5.6.2.4.2 Trucks current status will be displayable to the authorized system operators using SDMS workstations, using trucks ID numbers:

5.6.2.4.2.1  The unique, sequential “Truck ID” number (provided by the SDMS)
5.6.2.4.2.2 Truck LPR
5.6.2.4.2.3 Container number 
5.6.2.5 Notification to the drivers regarding their next destination shall be performed using the Variable Message Sign (VMS) via the SDMS Server’s internal queues. 
5.6.3 SDMS Reports

5.6.3.1 The supplied system shall include reports generator for the SDMS system.
5.6.3.2 The report generator shall provide a variety of reports, including statistical evaluation regarding:
· All events (inspections) for a particular date or during a defined period; (for example: time at site from entry to exit, Number of inspections, etc)
· All events related to a specific system or subject (Radiography/Manual, etc) defined in the system on specific dates or period
· All events of a particular category 
· All the activity and planning at the system on specific dates;
5.6.3.3 All site events shall be saved in the memory.

5.6.3.4 Final configuration and search capabilities shall be defined at the design reviews and approved by the Customer.

5.6.3.5 The contractor shall supply a suitable software program for producing history reports from the system, including all the relevant licenses.
5.7 SDMS workstations
5.7.1 The SDMS workstations shall be installed in the following locations.

a. Main Gate (G) cabins - check-out
b. Check-in cabins (A)  
c. Radiography operator/receptionist (D) 

d. Radiography  shift supervisor (D) 
e. Inspectors office (E)

f. Pit inspectors office (E)
g. Manual supervisor (E)

h. Site manager (E)

i. Control Office (E)
5.7.2 Specific authorization levels regarding re-routing of trucks, changing their status or destination shall be defined for each workstation/operator at the DR.
6. SECURITY & C.C.T.V SYSTEM

6.1 General

6.1.1 The security system shall be implemented, as part of site upgrade, following the requirements and descriptions in this chapter.

6.1.2 The security and CCTV system shall comprise of the following main subsystems:
a. C.C.T.V cameras in the radiography tunnel (safety operation).
b. C.C.T.V cameras in specific locations (operational reason)

c. PTZ cameras inside the site
d. Perimeter alarm system
e. C.C.T.V cameras along the perimeter fence
f. Security Command & Control system (C&C) to control and operate the alarm and C.C.T.V systems
6.1.3 Full integration between the alarm systems and the C.C.T.V system is required, i.e. when alarm occurs an automatic display of the relevant cameras occurs in the control room, including an automatic preset to relevant PTZ cameras.

6.1.4 Site gates
6.1.4.1 At site's gates detectors will be installed. It will be possible to neutralize these detectors during day time.
6.1.4.2 When detectors are not neutralized, crossing the gate will produce alarms even when the gate is not physically closed (For example: Active I.R detectors)     

6.1.4.3 Lighting system shall be installed for night time operation.

6.1.5 Security events in the site have priority over operational events.

6.1.6 Security Command and Control center shall be located at the following rooms:

6.1.6.1 Command and Control room in Building E - Main 
6.1.6.2 Command and control workstation in the gate cabin (G1) - Secondary
6.1.6.3 Preparation of Communication infrastructures for Command and Control workstation in the shelter room (E second floor) - Emergency
6.2 CCTV System
6.2.1 General

6.2.1.1 The C.C.T.V system will be based on IP technology and will meet all customer IT security requirements.
6.2.1.2 A separated communication net will be used for cameras and all security devices.

6.2.1.3 Recording

a. Recording will be 24/7.

b. Storage time - as defined in the table below (6.2.2)
c. Recording quality: high resolution, 25 fps.

6.2.1.4 Full integration between the alarm system and C.C.T.V system is required.

6.2.1.5 The control system shall be integrated with the security CCTV system in order to give possibilities of viewing and extended command.

6.2.1.6 The attach diagram presents the system principals.

6.2.1.7 C.C.T.V system workstations, display and operation) shall be installed at:

a. Security workstation (control room E)

b. Security workstation – site gate (G)

c. Radiography shift supervisor
d. Manual area shift supervisor
e. Site manager
f. Radiography operator (display of Radiography tunnel fixed cameras only)

6.2.1.8 Priority  
a. Priority of using the system (P/T/Z camera) is according to the order in the previous paragraph.
b. The security has the highest priority (Above all).

6.2.1.9 Final configuration will be approved at the design review meetings.

6.2.1.10 Technical requirements from the main devices are detailed below.
6.2.2 Area of coverage

The CCTV system will provide area coverage and storage time as follows:

	Serial No.
	Name/Description
	level of coverage
	Storage Time (days)
	Remarks/ Detection capability

	1
	Entry/Exit gate complex (inside and out)- area A and G
	100%
	90
	Ability to Identify truck's LPR and CC

	2
	Entry check-in cabins area
	100%
	90
	Ability to identify general activities in the covered area

	3
	Pre-radiography parking lot
	80%
	30
	Ability to identify general activities /movements in the covered area

	4
	Access roads/routes
"throughout the facility"
	80%
	30
	- refers to loaded/empty
trucks
- General activities in the area

· 

	5
	X-ray inspection building
	100%
	10
	The entire X-ray inspection process including the entire conveying process.
Ability to identify presence and any movement of any person in the tunnel (including driver's cabin and all area all around the parking truck, shielding doors, etc.)

	
	Entrance to tunnel (before and after entrance doors)
	
	10
	

	
	X-ray tunnel
	
	10
	

	
	Exit from tunnel (before and after exit doors)
	
	10
	

	
	Truck driver cabin
	
	10
	

	
	Harnessing and release positions
	
	10
	

	6
	Pre-clearance parking lot (waiting truck)
	80%
	30
	Ability to identify general activities /movements in the covered area

	7
	Manual inspection shed
	100%
	180
	Cameras-PTZ

Including unloading area

- ability to see into the container during unloading
Ability to identify general activities /movements in the covered area

	8
	Manual ins. Locked area
	100%
	180
	Ability to identify general activities /movements in the covered area

	9
	Pit area
	100%
	180
	Ability to identify general activities /movements in the covered area

	
	Pit area – Vehicles storage
	80%
	60
	Ability to identify general activities /movements in the covered area

	10
	Outside perimeter fence (security camera)
	100%
	10
	Ability to identify general activities /movements in the covered area


* Remark:  The coverage will be carried out using P/T/Z commanded cameras and/or fixed cameras as determined by the planner
[image: image1.jpg]siopejeq

fedsia  Aeidsig ey gous
ANLDD  suuely M
siopsieq

== A
- sol01u00 — weyshs
o
| — 1oA00 funoag
wung
wooy 0%d
AKiepuooag
selawes ays uj -

1

[ woums I siqlondo

Tondi 1 | B C |
Aunosg pejeslped | I N € I

fedsia  Aeidsig
ANLOD  suely

Lo

oM

[T

I

I

I

|

| [
| Jenieg R
I

I

|

|

|

%80 abeiois
®
SA

soey [eoluyos |

wopms

wooy 99 Uiy





7. Technical Requirements for system components
7.1 General

7.1.1 The technical requirements and definitions that appear in this Specification are the minimum required for each system / method separately and all together as a comprehensive system. 
7.1.2 The technical and operational performance of the subsystems and methods shall not deteriorate over the time and shall not be affected by ambient conditions on site.
7.1.3 Contractor's proposal shall include a detailed description of systems components, including technical specification. Final configuration and systems specifications shall be defined and approved at the DR meetings.
7.2 Fence alarm system
7.2.1 General 
7.2.1.1 The fence on which the alarm system shall be installed is a welded mesh fence
7.2.1.2 System type: an alarm system that uses vibration detection technology. 

7.2.1.3 The system detectors shall be address based. It shall be possible to adjust the sensitivity of the system's detection level. 

7.2.1.4 Definitions

7.2.1.4.1 False alarm - for this purpose, false alarm is an alarm received as result of no apparent reason. 
7.2.1.4.2 Irritating alarm - An alarm received due to conditions that the system should not have reacted to.  
7.2.1.5 System Requirements

7.2.1.5.1 The maximum number of false alarms shall be: 1 per week for the entire system. 

7.2.1.5.2 Detection reliability - 95%.
7.2.1.6 The Customer/CR is the entity that determines alarm type: whichever a false alarm, an irritating alarm or a real one.
7.2.1.7 Alarm display – the alarm computer shall be in the main security control room (Details in 7.7) with additional displays (secondary center). 
7.2.1.8 Final configuration shall be presented for Client's approval at systems design reviews.
7.2.2 System Structure
7.2.2.1 The perimeter alarm system shall have defined sections/zones. The alarm zones shall be determined in accordance with the following instructions:

a. An alarm zone shall be no more than 50 m. long. Specific distances shall be defined per detailed final design and upon Client's approval 

b. Each gate / side exit shall constitute an alarm zone.

c. In locations with poles close to the line of the fence (less than 2 m.) a vibration sensor shall be installed on the pole. The sensor shall have a separate indicator associated with the relevant section of the fence. 
7.2.2.2 One line of vibration sensors will be installed on the perimeter fence where the upright section is up to 2.5 m. high.  Where the upright section of the fence is 2.5 – 5 m. high, 2 lines of sensors shall be installed. The height at which the sensors are installed shall be coordinated with the supervisor/CR.
7.2.2.3 The amount and position of the sensors, fulfilling the operational requirements, shall be defined by the contractor and approved by the Client/CR.
7.2.2.4 A line of sensors shall be installed wherever spaces / conduits / openings are closed. 

7.2.2.5 The sensors shall be installed on the inner side of the fence (inside the site).
7.2.2.6 The communications and data collection units on the site shall be installed on a designated pole or fence post, inside the site.
7.2.2.7 All cabling for the alarm system, including the detector cables, communications and electricity cables, shall be connected in hardwired to the fence, by means of coated electrical wire or figure-8 clamps. 

7.2.3 Alarm indication
7.2.3.1 Indication of an alert shall be received separately from each section / vibration system sensor without any limitations regarding the number of alerted zones simultaneously.
7.2.3.2 User interface (authorized access controlled) will include an option to change/update algorithm's parameters adjusting system's sensitivity. The contractor shall detail which parameters are changeable and what is the optimal recommended status
7.2.4 Vibration sensors
7.2.4.1 The sensors shall use an address-based system, meaning; each sensor has an address of its own, including an option to define sensitivity / work status separately for each sensor.

7.2.4.2 The number of vibration sensors to be installed on the fence shall be the number required to obtain the necessary sensitivity and performance, both for receiving an alarm and for not receiving alarms and preventing false alarms. 
7.2.4.3 Preference shall be given to connecting the sensor cable and other cables for the system within the communications and data collection units installed on site.  External connections shall be soldered and cast with a shrinkable sleeve cover to seal them (against penetration of water and moisture), and they shall be installed on the fence with the opening facing downwards. 
7.2.4.4 Ambient conditions on the site shall not cause any change / deterioration in the performance of the sensors defined in this specification.
7.2.4.5 Sensors shall have a lifetime of at least 7 years from the end of the warranty period.
7.2.4.6 Installation of the sensors on the fence shall be solid in a way that they cannot be dismantled from outside the site. In any event, any attempt to disassemble a detector (to dismantle it or to change its status) shall alert the system.
7.2.4.7 The sensors will not be affected by the fence angle relative to the ground.
7.2.5 The system will alert in case of: 

7.2.5.1 Any attempt to cut, bypass or neutralize a communication cable.

7.2.5.2 Main supply or power supplier failure
7.2.5.3 Communication failure between system components
7.2.6 Shift to alarm mode
7.2.6.1 The vibration warning system will alert in the following cases:
a. An attempt of an individual person to climb on/over the fence.  The alert will be received when the person climbing the fence has reached no more than two-thirds of fence's height. 
b. When a ladder is placed against the fence and a single person attempts to climb over the fence. The alert will be received when the climbing person is outside the site. 
c. Attempt to cut the mesh fence
d. Attempt to saw through the mesh fence
e. Cutting wires (no more than 2 wires) that fasten the mesh to the poles.
f. When an attempt is made to disconnect the ties connecting the mesh/wires to the poles.
g. Attempt to dismantle parts of the system
7.2.6.2 The vibration warning system will not shift to alarm mode in the following instances:
a. Due to weather conditions at the site (wind, hail, rain, thunder).
b. When birds sit on or fly off the fence.
c. When a heavy vehicle passes close to the gate or the fence
d. When aircraft fly over the area of the site, including sonic booms
e. As result of EMI, RFI radiation 
7.2.7 All parts of the system shall comply with the following standards:
7.2.7.1 Temperature of -100 ÷ 600C for those parts of the system installed outdoors, and 00 ÷ 600C for other parts of the system. The system shall continue to function under these conditions as per all the requirements in the specification.

7.2.7.2 Humidity – equipments and parts of the system that are installed in a protected room or outside shall comply with work conditions of 95% relative humidity.  Any other components that are exposed to outdoor climatic conditions shall be waterproof.

7.2.7.3 Ambient conditions on the site shall not cause malfunctions, damage and/or false alarms, and they shall not interfere with the normal operation of the system.

7.2.7.4 The system shall be protected, there should be no false alarms and the normal operation of the system should not be disrupted due to induced voltages from RFI and EMI. The system shall not be disrupted or receive false alarms resulting from the operation of a mobile device with a transmission capacity of 35W and a frequency of 150 MHz at a distance of 2 m. from the fence or from any component of the system that is not installed on the fence. There must also be no interference of this kind when operating a mobile device with a transmission capacity of 5W and on a frequency of 150 MHz at a distance of one meter from any of the system components.

7.2.7.5 Electronic components that are located outdoors shall be encased in a suitable box, taking the ambient conditions into account (temperature, humidity, induced voltage). In his proposal, the contractor shall present the proposed casing for these components and the tests he has passed.

7.2.7.6 Any system components that are connected to communications lines, detector lines, video, coaxial wires, and power supply lines must be protected against power surges and lightning.  The protection components shall be installed at the ends of the lines, at the inlets and outlets of the various system control centers, of the end units, cameras and other electronic units spread over the site.

7.2.7.7 Surge-protector units at the ends of two-strand lines and communications lines shall be Poly phaser IS SPDDL and on coaxial lines shall be Poly phaser IS B75 or equivalent, performance to be approved by the client. To complete the protection, suitable grounding electrodes must be installed next to the end units and the service box casings along the fence. Grounding cables and shielding shall be connected to these electrodes.

7.2.7.8 The visual indicators on the computer shall be made of components that provide reasonable visibility in conditions of full light in the room.

7.2.7.9 In his proposal, the contractor shall specify what the MTBF of the operating system is, including the switchboard and peripheral equipment as required in the specification, specifying the method of calculating this information. 
7.3 HD IP fix camera, day/night 
7.3.1 Color network camera

7.3.2 Color photography in daylight conditions and monochromatic photography in illuminated night-time conditions, including automatic shift between modes.

7.3.3 RJ-45 connection to Ethernet 10Base-T/100Base-TX network.

7.3.4 CMOS/CCD 1/3" or 1/4" camera sensor.

7.3.5 Progressive scanning
7.3.6 H-264, MPEG-4 video compression
7.3.7 Protocol: TCP/IP, ICMP, IGMP, DHCP, HTTP, ARP, RTP, RTSP, RTCP, NTP, UDP unicast, UDP multicast

7.3.8 Resolution of at least 540 lines
7.3.9 25 fps in 1.3 megapixel mode
7.3.10 LUX sensitivity 0.1 in color, 0.5 LUX B&W at least (on F1.4 lens)
7.3.11 SNR (Signal to noise ratio) at least 50 db

7.3.12 Interlace: 1:2.
7.3.13 Shutter speed 1/1.5 - 1/30,000.

7.3.14 Automatic focus
7.3.15 At least 50 IRE
7.3.16 Dual stream

7.3.17 Dry contact in and out

7.3.18 Ambient conditions: -10(+50(C, 90% humidity.
7.3.19 Must work in outdoor conditions (IP-65)
7.3.20 Working voltage: 12/24 VDC Working support on PoE - Power over Ethernet 
7.3.21 Automatic white balance
7.3.22 CS/C mount lens, metal thread.
7.3.23 Cost of the camera includes license.

7.3.24  The supplied camera must be fully compatible and have an interface for working with an NVR to be supplied.

7.3.25  The camera must be made by a well known manufacturer, preferable a European/ Japanese or US manufacturer.
7.4 Lenses for megapixel camera
7.4.1 The contractor shall supply lenses consistent with the specifications below. The type and direction of the lens will be defined and approved at the time of installation on the site.

7.4.2 Varifocal lens compatible with megapixel cameras.

7.4.3 Compatible with 1/4" sensor or equivalent for 1/3" sensor
7.4.4 Focal length - 3-10 mm. or 5-50 mm

7.4.5 Aperture f/1.6 at least
7.4.6 The lens shall be made of polished glass.

7.4.7 CS/C mounts with metal thread.
7.5 PTZ – day / night IP camera (X36) 
7.5.1 Color network camera.
7.5.2 Color photography in daylight conditions and monochromatic photography in illuminated night-time conditions, including automatic shift between modes.

7.5.3 RJ-45 connection to Ethernet 10Base-T/100Base-TX network.

7.5.4 ¼" or 1/3" CMOS/CCD sensor.

7.5.5 Progressive scanning.
7.5.6 H-264, MPEG-4 video compression.
7.5.7 Protocol: TCP/IP, ICMP, IGMP, DHCP, HTTP, ARP, RTP, RTSP, RTCP, NTP, UDP unicast, UDP multicast.
7.5.8 Resolution of at least 540 lines.
7.5.9 25 fps in 1.3 megapixel mode.
7.5.10 LUX sensitivity 0.5 for color, LUX 0.1 for B&W at least (on F1.4 lens)
7.5.11 SNR: at least 50 db.

7.5.12 Interlace: 1:2.
7.5.13 Automatic aperture 1/1.5-1/30,000
7.5.14 Automatic focus
7.5.15 At least 50 IRE
7.5.16 Dual stream

7.5.17 Dry contact in and out

7.5.18 Ambient conditions: -10(+50(C, 90% humidity.
7.5.19 Must work in outdoor conditions (IP-65)
7.5.20 Working voltage: 220 VAC
7.5.21 Automatic white balance
7.5.22 Horizontal tilt angle: 360( continuous.
7.5.23 Vertical tilt angle: +30 ( to -80(.
7.5.24 Speed of horizontal tilt: 1-100(/second.  Varies according to operation
7.5.25 Vertical tilt speed: 1-20(/second.  (30(/ second in preset modes), varies according to operation.
7.5.26 3.3-119 mm. optical zoom lens (x 36) at least. Refers to ¼" CCD
7.5.27 Cost of the camera includes license.

7.5.28 The supplied camera must be fully compatible and have an interface for working with an NVR to be supplied.

7.5.29 In the X-ray inspection tunnel the camera equipment will be protected against radiation disturbances.
7.5.30 The camera must be made by a well known manufacturer, preferable European, Japanese or US manufacturer.
7.6 NVR recording / operating switching system
7.6.1 General requirements
7.6.1.1 The contractor will supply a CCTV system with switching, routing and recording capabilities. The system to be supplied will include all the necessary components: server, means of storage, screen, keyboard/keypad, operating measures, software, etc.

7.6.1.2 Number of cameras (estimated) - 50
7.6.1.3 The video signal to the system shall be transmitted on IP infrastructure. The communication net for cameras/security shall be a separate net.
7.6.1.4 The system software program shall be installed on computers with an up-to-date Windows operating system, shall facilitate real-time video surveillance as well as viewing of archived recordings. Different levels of surveillance will be possible, adapted individually to the end user.

7.6.1.5 All the video cameras will receive, record, store and route pictures to the system screen and/or accompanying screen.

7.6.1.6 The system will facilitate real-time viewing of video sources as well as playback and search simultaneously without any interference between the two activities.

7.6.1.7 A password (authorization) mechanism is required to allow the system administrator to define passwords for different users.

7.6.1.8 The system shall be operated from a client operating station.

7.6.1.9 The system will support the entire range of cameras which are connected to it, including PTZ cameras.

7.6.1.10 The system shall be expandable.

7.6.1.11 The system to be supplied will include all the permits / licenses required for full operation. Including client licenses for 20 operating stations
7.6.2 Technical requirements
7.6.2.1 Archive storage will be based on storage on local disks and shall support storage on NAS/SAN/DAS.

7.6.2.2 The system must support the updated Windows operating system.

7.6.2.3 High-quality recording of color video signals
7.6.2.4 Each server will handle 35 cameras (at most).
7.6.2.5 Continuous, round-the-clock recording (24/7/365) of all information channels 
7.6.2.6 Capable of storing data according to the required periods, as specified in clause 6.2.2. 
7.6.2.7 FIFO-based saving mechanism

7.6.2.8 During a synchronized playback from the archive, the user shall be able to simultaneously operate functions such as Fast Forward, Rewind, and jump to specific time points - so that this procedure occurs simultaneously on the video of the cameras on synchronized playback.

7.6.2.9 Hebrew interface for surveillance and configuration of the system is required.
7.6.2.10 A full back-up of the files must be kept. Category Raid Level 5, recording on N hard drives + back-up drive + system administration drive
7.6.2.11 Video signal recording data:
a. At least 25 frames/second per channel.

b. Megapixel camera recording as defined in this specification based on the camera's maximum speed. 
c. Resolution – at the same level of viewing resolution
d. The system shall have an option for defining at least 3 resolution levels: low, moderate, high (4 CIF).
e. At least 256 shades of gray. 16 million different colors.
7.6.2.12 The system shall be capable of supporting cameras of up to 8 mega pixels.

7.6.2.13 USB and SCSI ports for CD-RW ROM support or RW DVD for copying and backing up files
7.6.2.14 Standard compression - h264
7.6.2.15 The system must support ONVIF for maximum compatibility and flexibility, in favor of interfacing with standard systems in the future.

7.6.2.16 The system must support Dual Stream mode for surveillance and recording of different qualities. This capacity will also facilitate choosing the recording quality which will be saved for a longer period.

7.6.2.17 All the information channels shall be synchronized, including during reproduction.

7.6.2.18 Option to display real-time picture + pre-alarm picture from select cameras
7.6.2.19 Option to watch up to 16 channels simultaneously
7.6.2.20 Each channel shall contain all the information required for locating and identifying it.
7.6.2.21 Common, shared time clock for the entire system
7.6.2.22 Ability to fully operate and control PTZ camera system
7.6.2.23 Option to set up input for each video channel at the following levels:
a. Brightness
b. Contrast
c. Color
7.6.2.24 Input identification – the system shall contain a mechanism for integrating text at each entry with the following features:
a. Option to combine letters and numbers
b. 16 characters per channel
c. Hebrew font (preferable)
d. Option to set dark background
7.6.2.25 Option to save recorded files/ segments for a longer period by downloading to a disk/DVD
7.6.2.26 Alarm input for each channel to allow changes in the recording parameters.

7.6.2.27 Outlet connections to the network – the system shall have an outlet that hooks up with the TCP / IP network.

7.6.2.28 The system will contain a password mechanism to prevent an operator from changing the system setup and to prevent unauthorized operators from deleting files.
7.6.3 Operation of the recording system
7.6.3.1 Operation of the recording system, surveillance, file download, etc. shall under no circumstances interfere with the system's recording operation.

7.6.3.2 On-going control and operation of the recording system shall take place from a designated position on the recording system.
7.6.3.3 All system operations will be accompanied by feedback to the operator regarding the nature of the operation he is performing, the on-screen display mechanism, or equivalent.
7.6.3.4 The system's interface should be user friendly and will be operated by means of icons or by operating menus, etc.

7.6.3.5 The operating screen will be based on a map of the site and shall include all elements relevant for icon-based operation, such as: cameras in the area under surveillance, etc.

7.6.3.6 It must be possible to position and place the icons that appear on the screen spatially, as necessary. For example: the icon for a camera in the corridor shall also indicate its filming direction.
7.6.3.7 Each icon will contain its relevant information. Each icon will have an information table with its operating options. The table will contain information such as: name of the camera, its location, filming data, etc. The information table will be operated by right-clicking on the mouse.

7.6.3.8 The operator shall be able to playback files saved on the hard drive at any time without this affecting the recording process. Response time from making the request until the playback commences shall be no more than 3 seconds.
7.6.3.9 The following shall be possible when the video signal is played back:
a. Zoom-in on the picture.
b. Freeze the picture.
c. Fast forward and rewind
d. Control over color, contrast and luminance.
e. Simultaneous display of several synchronized pictures.
7.6.4 Requirements for operation of cameras
7.6.4.1 The system shall control the PTZ cameras and zoom lenses.   
7.6.4.2 Full control of all directions: up, down, left, right.
7.6.4.3 Full control of focus and zoom
7.6.4.4 Operation by means of a joystick
7.6.4.5 Capable of issuing a command for RS-485 cameras or corresponding
7.6.5 Support on VMD and analytics:

7.6.5.1 The system will interface with advanced end products for VMD and analytics, such as IOI, Agent VI, and others. The supplier must present existing interfaces.

7.6.5.2 The system shall facilitate the integration of end equipment for analytics and a concentration of analytic scenarios so as to create events in the system and generate alerts.

7.6.5.3 The terminal operator shall be able to "arm" and "disarm" the analytics mechanism on the terminal equipment via a surveillance program interface.

7.6.5.4 The surveillance interface shall display analytics scenarios in real time, including an option to display the tracking of an object, mark its movement, indicate the trail, etc.
7.6.5.5 The administrator interface shall enable, at least, the following actions:
a. Definition of IP addresses and parameters for cameras, compressors, and de-compressors
b. Definition of parameters for video bandwidth
c. Full management of access authorizations and passwords  

d. Timing of archive storage for each camera

e. Number of days during which video recordings from cameras shall be saved.
f. Duration of storage before and after an event (per camera)
g. Parameters of recorded video data or live data (per camera)
h. Network (multicast communications, multicast communications via server or UDP protocol per camera).
i. Definition of activities based on system events.

j. Definition of photography sites and groups of cameras on the site.
7.6.6 Production
7.6.6.1 The system shall provide the user with all the measures required to retrieve and save files on a disk / DVD, flash drive, external HD.
7.6.6.2 The control station shall contain all the equipment (burner, converter, etc.), software and apparatus required for proper operation.
7.6.6.3 The contractor will provide software packages that enable all the files saved on disk to be played on a PC, up to a quantity of 10 units.

7.7 Security Command & Control 
7.7.1 General 

The security systems Command and Control (C&C) system shall coordinate, display, handle and operate the following: 

7.7.1.1 Receive, display and handle alarms from the entire range of detectors and sensors in the system.

7.7.1.2 Control and operate the system's CCTV cameras.  

7.7.1.3 Be able to operate processes interfacing with the system, consistent with the capability of involving processes, for example:  intercom, activate equipment, access control, etc. 

7.7.1.4 Playback of the CCTV recording system, production of reports according to various cross sections as well as an "event portfolio" producing as per operator's instructions. 

7.7.1.5 The supplied system, including the work stations, shall include all the permits / licenses required for its full operation as well as routine updates as part of the comprehensive service and maintenance.
7.7.1.6 Contractor's proposal shall include a detailed description system configuration, including computers and servers technical specification. Final configuration shall be defined and approved at the DR meetings.
7.7.2 C&C workstation Configuration
7.7.2.1 The computers and systems that require memory must be supported by a UPS system as per the requirements in this specification. 
7.7.2.2 The operating workstations shall be PC based and shall include all designated software programs required for operation, control, maintenance, calibration, etc. only.

7.7.2.3 The workstations shall contain processes for connecting at least 4 screens.  It must be possible to use all the software programs described in this chapter on all the screens.  
7.7.2.4 The designated software programs in the C&C system shall operate through the Windows operating system, in Hebrew.  The contractor's proposal shall specify the proposed programs.

7.7.2.5 The C&C system must be capable of handling and managing at least 20 CCTV displays concurrently. 

7.7.2.6 The supplied computers shall comply with the requirements listed in this specification. The computers shall have internal and external memory components that are adequate for their function and for the number of messages that must be kept in the database.  All data shall be collected using the FIFO method. The computer hardware that is supplied must be the most up-to-date available at the time of supply. 

7.7.2.7 The system printer shall be connected to the system server (directly or via the network). Data or reports shall be printed per request.

7.7.3 System main features and requirements:
7.7.3.1 The C&C software shall include a diagram/aerial photograph/map of the site and be capable of zooming in on the diagrams on a larger, more detailed scale. 
7.7.3.2 Icons shall appear on the diagram clearly describing the systems/processes/equipment installed on site and their status – active and in working order, shut-down, alarm, out of order, etc.

7.7.3.3 It shall be possible to define a detailed treatment process for any alarm in the system, as follows:

a. Definition of which of the system workstations the alarm will be displayed
b. Definition of the chain of response required for each alarm.

c. Definition of which processes are to be activated (automatically) when an event occurs
7.7.3.4 When an event occurs, the system shall automatically display pictures that are relevant to that event, including real time pictures from the relevant camera/s and a pre-alarm picture, respectively.

7.7.3.5 All text information in the system: Data, menus, operating instructions, help screens, shall be in Hebrew.

7.7.3.6 Each detector's work mode (ready/neutralized) shall be defined separately. The status of each detector shall be clearly displayed on the site map. 

7.7.3.7 Each detector shall have an accompanying text box, mouse activated. The text box shall contain a brief description of the relevant component.

7.7.3.8 The system shall comprise of a main and a secondary workstation. The system shall provide flexibility regarding the definition of display, operation and treatment preferences between the different stations,  including definition of which workstations handle a particular event and which workstations are prioritized in activating processes, for example: control of PTZ cameras.

7.7.3.9 When several events must be dealt with simultaneously, the following will be performed:

7.7.3.9.1 The initial alarm automatically zooms-in on a map of the area of the event and displays a line in the table of alerts.

7.7.3.9.2 The alert immediately displays a set of cameras according to the definition.

7.7.3.9.3 The second alarm displays another line in the line of alerts.

7.7.3.9.4 The second alarm generates a display of another set of cameras, provided that there is a free screen/space available for the display.  If there is no available screen/space, generation of the pictures will wait.

7.7.3.10 When the event has been dealt with and a screen/space becomes available to display the cameras, the cameras waiting in line will automatically generate their display.

7.7.4 CCTV operation 

7.7.4.1 Operation shall be simple and user friendly. The operator shall operate the CCTV system from the system screen and main alarm display.
7.7.4.2 Operation shall be by means of icons or operating menus, etc.
7.7.4.3 The operation shall be based on a map of the site and shall include all elements relevant for icon-based operation, such as: cameras in the area under surveillance, alarms, etc.
7.7.5 Interfaces with related systems:
7.7.5.1 Interface with related systems (alarms, CCTV, access control, etc.) shall be based on a detailed protocol between these system and the C&C system. 

7.7.5.2 Interfacing with the C&C system will facilitate:

a. Automatic generation of a picture depending on the event
b. Full operation of the CCTV system as described in this chapter. 

c. Full investigation of the recordings database
d. An option to download/ copy (burn) files.

7.7.6 Indication, operation and control 
7.7.6.1 At Systems Design Review the Contractor shall present for Client approval system's configuration, specifically referring to the following items: 
7.7.6.1.1 Display and basic operation
7.7.6.1.1.1 The system's display shall be based on an aerial photograph / map of the site and shall include indications.  The scale of the site will be emphasized on the drawing and each section will be marked on it separately.  Icons will be defined for the alarm system as well as detectors and processes on the site, and the surveillance zones for the CCTV cameras will also be defined.
7.7.6.1.1.2 All events shall be saved. 

7.7.6.1.1.3 The system shall include reports production 
7.7.6.1.1.4 Sensitivity of the different system sensors/detectors will be adjusted and calibrated from the C&C station.  The system manager (security officer) shall have an access code to perform this action. 

7.7.6.1.2 Indication
a. Audio indication 

b. Visual indication: displayed icon on site's map, changing colors/event status and category, fixed or flashing display, etc. 

c. Close-up capabilities - displaying detailed maps/drawings of alarm area. The contractor shall submit a diagram of the display and the various drawings that appear in the close ups for the client's approval. 

d. Text display

e. The number of messages in the system 
f. The wording of the messages shall be coordinated with and approved by the client. 
7.7.6.1.3 Operation method (icons, mouse, keys, etc)
7.7.6.1.4 Alarm mode operation 
7.7.6.1.5 Indication and operation in frequent malfunction situations
7.7.6.1.6 Reports 

The system shall include printed and on-screen reports, referring, at least to: 
· Events on a particular date or during a defined period
· All events from a specific system or section/zone or from several sections/zones defined in the system on specific dates.
· All events of a particular category – such as all the alarms, all the OFF/ON messages, etc. (on specific dates) 
· All the activity and programming at the control center on specific dates.
· Shift between day/night modes. 

Final configuration shall be defined at the DR.
7.7.6.1.7 Access Control


The system shall have several safety access levels that allow/disable various operations and programming, consistent with the user's security level and function:
a. Level 1 – operator level 

b. Level 2 – superior's level.
c. Level 3 – technician level.
d. Level 4 – manager's level, security officer.
Each level operation's shall be defined at the DR meetings.
7.7.7 Client Computer configuration 
7.7.7.1 Contractor's supplied computer/server shall be adequate to fulfill the operational requirements of the system. The proposed configuration shall be presented for approval at the DR meeting.

7.7.7.2 Following is the minimal basic configuration (for reference only):
7.7.7.2.1 Motherboard – Intel ATX, most up-to-date version, Intel Pentium Dual Core processor (including Intel warranty certificate), with a frequency of at least 3 GHz An Intel active cooling kit shall be installed on the processor.
 The motherboard shall include installed memory of at least 2 MB.  The board shall contain an integral sound card.
7.7.7.2.2 The 2 GB DD R2 motherboard shall include (at least) integrated controllers, as specified below: 
a. Controllers for EDI hard drive, with a PCI interface. 

b. USB ports.

c. DVD SATA burner at least.

d. ATX MIDI tower case compatible with the motherboard, with available space for two additional 5" devices at least. The case must be safe and fitted with an extra fan in addition to the one supplied by the contractor.  The case and supplier must appear on Intel's recommended list. 
e. SATA 500 GB hard drive at least. 

f. Hebrew/English engraved keyboard with 104 keys (known brand) connected without an adaptor.  

g. Mouse, including literature, drivers, and a mouse pad.

h. PCI Express 512 MB graphic card
7.7.8 The contractor shall undertake to install revised versions of the alarm system for at least 7 years from receipt of the system

7.8 Security requirements for computer systems
7.8.1 The security systems for the site and control rooms will be administered using a domain controller (DC) server and backup server, which include a Windows updated operating system, including client licenses for all the computers.  

7.8.2 The security system will include the following modules:

7.8.2.1 Applications control module, for applications approved by the system administrator.  

7.8.2.2 Device control module for integral and portable devices
7.8.3 Basic requirements for the applications control module:

7.8.3.1 Only approved applications may be used.

7.8.3.2 Option for fast access to applications, without the need to reboot the computer or exit the system.

7.8.3.3 Ability to change access authorizations on the spot.

7.8.3.4 Ability to copy a current list of authorizations onto external magnetic media for backup and continuous protection. 

7.8.3.5 Ability to keep a record of and document user requests to operate approved and non-approved applications.

7.8.3.6 System administrator activity must be recorded and documented.

7.8.3.7 Ability to establish a standard system response if a non-approved application is used - operation or blocking. 

7.8.4 Requirements in principle for the device control module:

7.8.4.1 The operating system shall be protected by means of an access control system which restricts user access to devices and system components. 

7.8.4.2 The system must provide protection against viruses, Trojan horses, worms, and unknown monitoring programs (illegal or unauthorized) in the system.
7.8.4.3 The system will provide command and control over the transfer of data to devices authorized by the system administrator by receipt of a copied file name or full copy of that file when memory content is copied.

7.8.4.4 Following is a description of the key properties and specifications required:

a. Ability to manage a list of authorizations (passwords) for each user and group of users
b. Ability to define special passwords for a specific computer or device
c. Prevent use of unauthorized devices and those with which the system is unfamiliar.

d. Ability to use approved devices for operation only.

e. The system should be able to provide a special ID number for each device.

f. Ability to provide access, reading and/or writing.

g. Ability to time access to a particular device in advance and for a given time.

h.  Ability to provide temporary access to a specific device.

i. Ability to create a library of DVDs/CDs and passwords for users or groups of users.

j. Ability to create lists of portable media with special ID numbers and user passwords.

k. Option for each user to use portable media by means of encrypted systems.

l. Update list of authorized file signatures for each log-in to the system.

m. Ability to change access authorizations immediately.

n. Ability to backup the current list of passwords on a desktop or laptop which is not connected to the network, thus providing continuous protection. The file will be updated when the computer is reconnected to the network.

o. Ability to limit the quantity of data which is copied from a particular computer (or network) onto a PSD (portable media or disk).

p. Support is to be provided for the following devices:

· Hard drives

· Biometric  devices

· Modems

· Wireless network cards

· Digital cameras

· DVD/CD burners/players

· Scanners

· Flash drives

· USB printers

q. Support is to be provided for the following devices:

· USB

· LPT

· Fire Wire
· Blue tooth
· Wi-Fi

· IrDA

· PCMCIA

· COM 

· IDE 

· S-ATA

7.8.5 Security System Server– minimum configuration:

7.8.5.1 The server will be HP DL 360 G7 or equivalent.

7.8.5.2 Processor Core: Dual and Quad

7.8.5.3 Processor Cache: 5500 series 4 MB to 8 MB Level 2 Cache depending on processor

7.8.5.4 Processor speed: 2.93 GHz

7.8.5.5 Front Side Bus Speed 800 to 1333 MHz.

7.8.5.6 Memory Type: PC3-10600R Registered (DDR3) Memory or PC3-10600E Un buffered (DDR3) Memory.

7.8.5.7 Standard Memory
Performance Model: 12 GB (6 x 2 GB) DDR3-1333 MHz Registered Memory
Base Model: 6 GB (3 x 2 GB) DDR3-1333 MHz Registered Memory

Entry Model: 4 GB (2 x 2 GB) DDR3-1333 MHz Registered Memory

Efficiency Model: 4 GB (2 x 2 GB) DDR3-1333 MHz Un buffered Memory          
7.8.5.8 Memory 144 GB Registered Memory (48 GB Un buffered Memory)

7.8.5.9 Memory Slots 18 DIMMs
7.8.6 Security system WS - Minimal Configuration
7.8.6.1 Chip set motherboard X58.

7.8.6.2 Intel Core I7 2.66 GHz processor, an Intel active cooling kit must be assembled on the processor. The motherboard shall include installed memory of at least 2 MB.
7.8.6.3 8 GB RAM, DDR3 1600  
7.8.6.4 Sound card.

7.8.6.5 Network card 10/100/1000
7.8.6.6 Controllers for EDI hard drive, with a PCI interface. 
7.8.6.7 4 USB ports.
7.8.6.8 DVD SATA burner at least.

7.8.6.9 ATX MIDI tower case compatible with the motherboard, with available space for two additional 5" devices at least. The case must be safe and fitted with an extra fan in addition to the one supplied by the contractor. The case and supplier must appear on Intel's recommended list.

7.8.6.10 500 GB SATA hard drive at least. 
7.8.6.11 Hebrew/English engraved keyboard with 104 keys (known brand) connected without an adaptor.
7.8.6.12 ATI or NVIDIA GeForce 1 GB screen card, including HDMI connector;
7.8.6.13 WIN 7 operating system, 64 BIT
7.8.6.14 The contractor shall install the updated versions of the system software, for at least 7 years from system acceptance. Upgrading of the versions is part of the comprehensive service and maintenance contract.

Note: Contractor's proposed configuration will be examined for approval or a revised version will be supplied in coordination with the contractor.
7.9 OCR

System (OCR) required in all places were container recognition is needed
section 6-G.DOC
6G-1
2012
27
section 6-G.DOC
6G-42
2012

