
LIGHT VEHICLE RADIOGRAPHY SYSTEM
 Section 6C1


SECTION 6 - SUB-SECTION C1
COMMUNICATION INFRASTRUCTURE, TELEPHONE SYSTEM AND PUBLIC ADDRESS (PA) SYSTEM

CONTENTS


21.
Scope of Work


112.
Installation, Operation and Training


123.
Service and Maintenance


134.
Documentation


145.
Ambient Conditions


156.
Requirements for information Security and Security training




1. Scope of Work

1.1 General 

The Contractor shall design, supply and install the communication infrastructure for the Inspection Site accordance to the International, Israeli Communication and Bezeq standards. 
1.2 Communication Systems to be installed

The communication systems shall be installed for four separated purposes:

a. “Telephony”, “Data” and “PA system communication.

b. “Customs Data” communication.

c. Radiography System communication

d. Security & CCTV communication - infrastructures shall be defined by the contractor (outdoor & indoor).

1.3 Communication Infrastructure Content

All cables in this section will be in different color than the cables of the radiography system. 

All labels, patch cords and outlets will be in different color than the cables of the radiography system. 

The communication infrastructure shall consist of the following:

1.3.1 Outdoor Communication to the Site

1.3.1.1 The site shall be connected to the outside Bezeq communication facility by:

a.  Fiber optic cable – 2 cables of 48 fibers – 24MM +24SM. The terminations of these cables will be in the radiography building and in the customs building. The termination will include all needed equipment/ elements. The cable will be shielded for outdoor installation.
b. Copper multi pair cable - 2 cables of 50 pairs -50x2x0.6 PJ. The terminations of these cables will be in the radiography building and in the customs building. The termination will include all needed equipment/ elements. The cable will be shielded for outdoor installation.

1.4 Outdoor Communication Ducts and Cables

1.4.1 Main communication room connections  
1.4.1.1 Customs Data System (CDS) - The main communication (CDS) room is located at the customs office in the customs building. The following buildings will be connected to the main communications room:
c. Radiography building (entrance/ exit). 

d. Manual pit (MP).

e. Each gate (entrance/ exit). 

f. The customs office at the arrivals hall. 
g. Camera poles and perimeter fence.

1.4.1.2 A minimum clearance of 60 cm shall be maintained between the Customs Data (red) communication ducts to the other communication systems ducts. 

1.4.1.3 A minimum clearance of 100 cm shall be maintained between the communication ducts and any other conduit such as RF, power etc.  

1.4.1.4 At the building entrance, the ducts shall have a bend radius of at least 1.1 m.

1.4.2 Cable installation
The Contractor shall supply and install the following outdoor communication cables:
1.4.2.1 Internet Data Fiber Optic cables 

a. From main customs data communication room in the CDS room:

· by a 12 Fibers 50µ MM (multi-mode OM4) to R.
· by a 6 Fibers 50µ MM (multi-mode OM4) to exit gate.
· by a 6 Fibers 50µ MM (multi-mode OM4) to entrance gate. 

· by a 6 Fibers 50µ MM (multi-mode OM4) to MP.
b. Outdoor Copper “Data” network cables S/STP GIGADOR 1000 MHz, CAT. 7A outdoor cables (products by Teldor or equal) will be installed from the communication rack in building R to the Manuel pit if the distance does not exceed 90 meters, 4 sockets.                                                        

 The fiber cables shall terminate at fiber optic panels with LC Connectors (products by Fibernet or approved equal).

c.  Installed on 19” communication racks.

d. Unused connector shall be sealed in order to prevent the fiber optic connector contamination.

[image: image1.emf]
1.4.2.2 Customs Data Fiber Optic cables

a. From main customs data communication room in the MCR room:

· By a 12 Fibers 50µ MM (multi-mode OM4) to CO building.

· By a 12 Fibers 50µ MM (multi-mode OM4) to R building.

· By a 6 Fibers 50µ MM (multi-mode OM4) to MP building.
· by a 6 Fibers 50µ MM (multi-mode OM4) to exit gate.
· by a 6 Fibers 50µ MM (multi-mode OM4) to entrance gate.
b. Outdoor Copper “Data” network cables S/STP GIGADOR 1000 MHz, CAT. 7A outdoor cables (products by Teldor or equal) will be installed from the communication rack in building R to the Manuel pit if the distance does not exceed 90 meters, 4 sockets.

 The fiber cables shall terminate at fiber optic panels with LC Connectors (products by Fibernet or approved equal).

c.  Installed on 19” communication racks.

d. Unused connector shall be sealed in order to prevent the fiber optic connector contamination.

e. [image: image2.emf]
1.4.2.3 Radiographic and C&C  Data Fiber Optic cables 

a. From main customs data communication room in the MCR room:

· By a 12 Fibers 50µ MM (multi-mode OM4) to CO building.

· By a 12 Fibers 50µ MM (multi-mode OM4) to R building.

· By a 6 Fibers 50µ MM (multi-mode OM4) to MP building.
· by a 6 Fibers 50µ MM (multi-mode OM4) to exit gate.
· by a 6 Fibers 50µ MM (multi-mode OM4) to entrance gate.
b. Outdoor Copper “Data” network cables S/STP GIGADOR 1000 MHz, CAT. 7A outdoor cables (products by Teldor or equal) will be installed from the communication rack in building R to the Manuel pit if the distance does not exceed 90 meters, 4 sockets. 

c. The fiber cables shall terminate at fiber optic panels with LC Connectors        (Fibernet or approved equal) installed on 19” communication racks.

d.   Unused connector shall be sealed in order to prevent the fiber optic connector contamination.

[image: image3.emf]
1.4.2.4 Security Systems cables

a. From main customs data communication room in the MCR room:

· By a 12 Fibers 50µ MM (multi-mode OM4) to CO building.

· By a 12 Fibers 50µ MM (multi-mode OM4) to R building.

· By a 6 Fibers 50µ MM (multi-mode OM4) to MP building.

· by a 6 Fibers 50µ MM (multi-mode OM4) to exit gate.

· by a 6 Fibers 50µ MM (multi-mode OM4) to entrance gate.

· by a 2 Fibers 50µ MM (multi-mode OM4) to each camera. 

b. Outdoor Copper “Data” network cables S/STP GIGADOR 1000 MHz, CAT. 7A outdoor cables (products by Teldor or equal) will be installed from the communication rack in building R to the Manuel pit if the distance does not exceed 90 meters, 4 sockets. 

c. The fiber cables shall terminate at fiber optic panels with LC Connectors        (Fibernet or approved equal) installed on 19” communication racks.

d.   Unused connector shall be sealed in order to prevent the fiber optic connector contamination.

 [image: image4.emf]
1.5 Indoor Communication Ducts and Cables

1.5.1 Indoor communication installation

1.5.1.1 Duct dimensions and materials:

e. Ducts for the Radiographic and Security systems (BLACK) cabling shall be 30x8.5 cm (main routes) 20x8.5/10X8.5 cm (secondary routes). The ducts shall be wire mesh cable trays from stainless steel.

f. Conduits shall be 29mm diameter for each module in the box (for 4 sockets). 

g. Ducts for the Custom data communication systems (RED)

Cabling shall be 30x10 cm (main routes) 20x10 / 12X6 cm (secondary routes). The ducts shall be plastic PVC cable ducts. The minimum distance from red ducts to other systems should be 20 cm. The distance between red horizontal ducts and black racks should be 100 cm.
h. Conduits shall be 29mm diameter for each module in the box (for 4 sockets). 

i. In the main communication room, there shall be a galvanized steel ladder 30 cm wide above the racks and surrounding the room.

1.5.1.2 Main communication systems shall be installed in the ceiling or below the raised floor.

1.5.1.3 Duct width as well as vertical and horizontal bends shall accommodate suitable curving of all duct cables (45 (bend). 

1.5.2 Indoor Cable Installation

1.5.2.1    Racks 

a. The Contractor shall supply communication racks:

b. Floor racks (25”W x 100mmD x 44uH) In buildings R.

c. Wall racks (19”W x 100mmD x 10uH) In each gate and in the manual pit.

d. All racks on site shall include: sealed perforated door at the front and back with a lock , shelves for equipment, 24RJ panels, fiber optic panels, brush panels , 50 RJ45 telephone panels ,blank panels, shelves , vents, 6/12 electricity panels (PDUs) with CEE plugs 16A, grounding kit , and a bottom drawer 3U  height (for 44uH racks only). 

e. The contractor will make sure that the rack is installed in an air conditioned and ventilated environment.

f. The contractor will make sure that the rack is accessible after the installation.
1.5.2.2 Indoor Cables

Indoor Cabling communication system shall be installed in the building for network cabling – double S/STP GIGADOR 1000 MHz, CAT 7A (Products by Teldor p/n 99XG54XXX or approved equal)

1.5.2.3 Outlets 

        a.
 Standard communication outlets/sockets shall be provided in rooms for each customs workstation:

· Telephone – minimum 2 shielded RJ-45, CAT6A outlets, (products by RIT, R&M, Panduit, TE or approved equal).

· Customs Data – minimum 4 shielded RJ-45, CAT6A outlets, (products by RIT, R&M, Panduit, TE or approved equal).

Note: These Customs sockets will be installed at a distance of at least 1m from other systems outlets.

· At supervisor’s workstations (app. 15 rooms) an 8 sockets outlet will be installed for each system.

· Radiographic – shielded RJ-45, CAT6A outlets, (products by RIT, R&M, Panduit, TE or approved equal) according to contractors final plan.

1.5.2.4 Patch Panels

a.  Data copper patch panels will be S/STP RJ-45, CAT6A patch panels , ( products by RIT, R&M, Panduit, TE or approved equal) .

c.
   Patch panel for 12 / 24 optic fibers LC connectors (products by Fibernet or approved equal).

1.5.2.5 Patch cords

a. Copper CAT 7A patch cords – RJ45 to RJ45 connectors CAT6A both ends, CAT7A cable. The cords will be provided in 2 (two) different colors (for CUSTOMS DATA and RADIOGRAFIC systems). 
b. Fiber patch cords – 50µ MM (multi mode OM3/OM4). LC connectors at both ends.
c. Lengths, labeling and quantities of patch cords shall be determined (0.5 / 1 / 2 / 3   meters).

Note: Cables, outlets, panels and communication system parts shall be approved by the customer. The equipment shall be with accordance to the updated standards at the installation period with no additional cost.

1.4.2.6        SWITCHS – switches with 24/48 ports  (Juniper), including a MM Gigabit -SX–LC mini-gbic.
1.4.2.7 TV outlets – approx. 2 outlets shall be installed in TBD and shall be connected to a dedicated satellite antenna mounted on the roof (via Israeli satellite TV Provider Company “YES”).

1.4.2.8      Multimedia –  the screen that will be installed at the arrivals hall:

Communication infrastructures (VGA, Audio and HDMI cables) shall be installed in order to operate the screen from a panel located at the customs office. Specific location TBD. Connection of a computer to the  screen (The screen will be supplied by the contractor. The resolution will be at least 4K. The contractor will provide a ceiling mounting kit).
1.5.2.6 Marking and Signs

a. Communication ducts will be marked in HEBREW with clearly visible signs: “COMMUNICATION” / “DATA COMMUNICATION “. 

b. The signs shall be placed along the duct, with at least 3-m intervals and especially adjacent to all branching points and passages between rooms.

c. All communication outlets shall be marked with clearly visible labels (building-floor-number). Colors shall be given at the design stage.

2. Installation, Operation and Training 

2.1 Installation

  
The installation will be professional, expert and efficient using standard and safe materials and tools complying with Israeli Standards and work practices.

2.2 Acceptance Tests

2.2.1 The supplier will attach acceptance tests or specifications (copper pass test, fiber optic OTDR test) .

2.2.2 The tests will be conducted by the supplier in the presence of customer’s representative. Once tests are completed, the supplier will prepare a summary report. The supplier and the customer’s representative will append their signatures as mark of approval of the tests and their results.

2.2.3 All approvals will be under the responsibility of the supplier.

2.3 Maintenance Commitment


The supplier will be committed to stocking necessary spare parts for a minimum period of 10 years. 

2.4 Training 


Once the system is operating, the supplier will train the customer’s employees in system operation, features and capabilities. The training will be based on documentation provided to the customer. The customer will be able to order refresher courses and additional training for a period of 6 month from exchange start-up date, at no additional cost. 

3. Service and Maintenance 

3.1 Service
3.1.1 Supplier’s service center will be ready to provide telephone diagnostic and troubleshooting support. To this end, a professional will be available to respond to queries within 10 minutes from the call for service, or for telephone support.

3.1.2 Response time required for urgent failures - Technician arrival within 2 to 4 hours.

3.1.3 Ordinary failure response times -

a.
For failure message received before 11:00 the technician will arrive the same working day before 15:00. For failure message received after 11:00 the technician will arrive until 11:00 the next working day.

b.
The supplier will make sure the customer is available and the faulty equipment is accessible. No technician visit will take place without prior coordination.

3.2 Maintenance
3.2.1 The supplier will visit the site once every three months. The periodic inspection will include system, peripheral units, ambient conditions etc. Visit report will be submitted to the customer or as pre-assigned.

3.2.2 The supplier will keep a maintenance and event log.

4. Documentation  

4.1 While installing the system the supplier will attach the following documentation in Hebrew. 

4.2 He will be responsible for providing documentation and technical literature as follows:

a. Technical documentation – all equipment user instructions and specifications. This documentation will be forwarded to communication manager on special request within 24 hours. 

b. Operational documentation – equipment operating instructions, troubleshooting etc. This documentation will be forwarded to communication manager.

4.3 The supplier will provide the customer with 4 documentation sets including:

a. Technical specifications of system and interfaces.

b. System layout with connection and interface points.

c. Detailed user guide for operator and system manager allowing optimal system operation.

d. Operating instructions for end users.

4.4 Any other information and documentation pertaining to optimal operation;

4.5 The documentation will have a clear and good-looking graphic layout, incorporating advanced graphic features that facilitate reader’s comprehension. Documentation samples will be submitted on customer’s request.

4.6 The documentation will be submitted in a bound book format and, where possible, in Microsoft Word, Autocad, Excel compatible CD- ROM format.
5. Ambient Conditions

5.1 Required Conditions


The system with all equipment will operate under the following conditions:

a.
Temperature: -2(C to 60(C

b.
Relative humidity: 20% - 80%

c.
Dust: 14 mg/ m2
5.2 Grounding

The supplier will list the equipment grounding requirements and verify their compatibility at the site.

5.3 Compliance with Standards


The supplier will attach standards and compliance certificates for all equipment supplied (cables, patch panels, sockets, etc.).

The supplier will attach RFI/EMI compliance certificates according to IS 961, Articles 6.1 and 6.2 for any equipment supplied.


The supplier will attach safety compliance certificates according to Israeli Safety Standard 1124.

5.4 Lightning Protection 


All supplied equipment will be lightning and surge protected.


The protection will comprise: power sources, electrical sockets, data lines  etc. 

6. Requirements for information Security and Security training
6.1 The nature of the activity in the Customs and VAT Division requires special emphasis on information security.

6.2 The tender will be executed subject to the security conditions customary in the Ministry. The Ministry may from time to time change and redefine these terms and the Bidder undertakes that if its bid is chosen as the winner of the tender, it will meet all of the security conditions as determined by the Ministry without additional consideration.

6.3 The Customs and VAT Division is a governmental body that is subject to various security directives, and performs activities performed by or at the office for compliance with security classification requirements prior to its implementation.

6.4 In general, the level of security classification in which employees are required to stand on the winner's behalf is according to the relevant definition for each case and the level of exposure of the winner against the level of the project's classification. The Ministry reserves the right to disqualify any employee at its sole and absolute discretion, and if the Ministry decides to disqualify employees on behalf of the winner, there is no disqualification in order to release the winner from fulfilling all his obligations in the tender.

6.5 Top of Form

6.6 The Supplier's access to data owned by the Tax Authority will not be possible. 
6.7 The winner will not collect Information owned by the customs with a high level of security as defined in the Privacy Protection Regulations Second addition: No illegal production or use of databases will be created or used.
6.8 The winner is prohibited from transferring to any third party any information that he will receive as part of the engagement in this tender or to do any use of the information to which he was exposed in connection with the execution of this tender for any other purpose that is not directly related to perform its obligations as part of the execution of this Tender and after approval by the Ministry.
6.9 During the performance of the tender, the winner will undertake all security measures in order to ensure the security of all the material that will reach him as part of the execution and will present the means taken at the request of the ministry’s representative. 

6.10 The winner is required to report immediately to the office within 2 hours of the event on any security issue, the information including information leakage. In this case the winner must act to prevent
leakage of information and any damage resulting from the failure.

6.11 At the end of the engagement, the winner must transfer to the Ministry all the information accumulated during the performance of the tender all in accordance with the above instructions and instructions.
Begin-Terminal Site SOW

Section 6-C1_Infracstructure.doc
    6C1-1

      2019

