27

SECTION 6 - SUB-SECTION G

SPECIFICATIONS OF THE FCS (FACILITY CONTROL SYSTEMS)

CONTENTS

1. General………………………………………………………………………………………
2. Purposes of The Site Control Systems…………………………………………………..

3. Facility Control System (FCS)…………………………………………………………….

4. Radiation Control System (RCS)…………………………………………………………

5. Shipment Directing and Monitoring System (SDMS)…………………………………..

6. OCR Truck gate Systems…………………………………………………………………

7. Parking Control System……………………………………………………………………

8. Security & CCTV Systems………………………………………………………………...

9. Technical Requirements for System Components……………………………………..

Appendix A: IP cameras and CCTV standard……………………………………………..

Appendix B: Information & Cyber Security…………………………………………………   



1. General

1.1 The facility in its entirety includes various systems, each working separately at a different level of automation and including various backup possibilities. The availability and reliability of the systems constitute an indispensable condition for the proper and continuous working of the designated equipment installed in the facility.

1.2 The various control systems will give an up-to-date real-time status report of site's systems and vehicle traffic and will caution regarding deviations from routine. The control will operate backup systems and will allow coping with emergency situations (radiation, fire, etc.).

1.3 Command and control of the site will be provided mainly by the following Three (3) main systems, each fulfilling a different function:

1.3.1 Shipment Directing and Monitoring System (SDMS) - Traffic Control System (TCS)
1.3.2 Radiography Control System (RCS)

1.3.3 Security Systems;
1.4 Each one of these systems should function as a stand- alone system, the first two control systems (SDMS and RCS) comprise the FCS.

1.5 The Contractor shall present system’s configuration at the various locations/positions as required at the DR meetings. 

1.6 Acceptance tests protocol for each system shall be presented by the Contractor for Client's approval.

1.7 The subcontractor for the Security and SDMS systems and subsystems shall be an Israeli integrations company with proven service and maintenance capabilities.
1.8 The Contractor is responsible for the implementation, testing and training as well as the service and maintenance of these systems. 

1.9 Thunderstorm / Lightning Protection 

1.9.1 All supplied equipment will be lightning and surge protected.

1.9.2 The protection will comprise: power sources, electrical sockets, data lines etc.
1.10 All equipment will provide continuous operation in no power situations, using UPS and connection to facility generator.

1.11 All supplied equipment, designed for outdoor and indoor installation, shall comply with the weather and environmental condition as specified in Section 2 and its operation will not be affected by environmental conditions.
1.12 Contractor's proposal shall include a detailed description of the systems configurations and technical specification, including computers and servers. Final configurations and systems specifications shall be defined and approved at the DR meetings.
1.13 An information security project manager will be appointed by the contractor. This project manager will oversee implementing the SIEM software and all other information security aspects of the project. The requirements for this function are described in appendix B. The information security manager will be approved in advanced by the customs information security team. The contractor will attach the information security project manager CV and experience to the tender documents for review. The customs information security team reserves the right to interview the proposed project manager if it will be needed.
1.14 All sub-contractors will be approved by the customs information security and physical security teams. 
1.15 The contractor will describe the possibilities for future developments. The contractor will provide the SDK interface at a cost determined in advance for any future development requested for a period of 7 years.
1.16 It should be noted that the contractor must work under the guidelines of the customs information security department, which are updated from time to time.
2. Purposes of the Site Control Systems

2.1 The purpose of the Command and Control of facility systems is:

2.1.1 To ensure and control site safety

2.1.2 To control vehicle traffic at all stages of the work at the site

2.1.3 To control and efficiently operate the X-ray inspection installation and the manual site
2.1.4 To ensure and control site security (including access control system) 

2.2 To present at the required workstations the relevant data regarding cargo contents and to provide maximum information and instructions defining the inspection required.

2.3 To efficiently cope with emergency situations and deviations from the routine by appropriate warnings or/and intelligent operation of backup units, either by automatic or by manual operation
2.4 The system will make it possible to locate faults and repair them within pre defined periods of time. 
2.5 To serve as a tool of control access to the facility/buildings or rooms and to integrate into the overall safety and security systems of the facility;
2.6 To provide an up-to-date status report on the status of all the systems to relevant agencies in the facility.

2.7 To serve as a tool for cumulative information, trends and characteristics of the systems in the buildings, for purposes of analysis of behavior, drawing of conclusions and raising the level of performances and reliability of the systems on the basis of "historic" information and locating of failures.

2.8 To serve as an objective and reliable tool for analysis of failures, their causes and characteristics, as a basis for the engineering analysis of the faults and an attempt to prevent them in the future by changing of parameters or drawing of operational conclusions.

2.9 To serve as an engineering aid for support of the system operation and maintenance;
3. Facility Control System (FCS)

3.1 The Facility Control system comprises of: 

3.1.1 Radiographic control system (RCS) 

3.1.2 Shipment Directing and Monitoring system (SDMS) including the Traffic Control System (TCS) 


Thus, the FCS controls all the operational processes taking place at the site.

4. Radiation control system (RCS)

4.1 The RCS deals at the command and control level with the following elements:

4.1.1 Operation of all the safety means of the radiation system

4.1.2 Operation of the X-ray inspection system.

4.1.3 Suspension of X-ray on conclusion of the scanning process.

4.1.4 X – Ray Image acquisition, analyzing process and Image Data base updating.

4.2 The X-ray inspection control system shall work in functional integration with the traffic control system (SDMS). In addition, data transfer from RCS to the SDMS will be provided.

4.3 The system software shall include all the routines required for sustaining the conditions and proper operation as regards of operation and safety.

4.4 The system will contain appropriate backups for operational compliance with very high safety requirements.

4.5 The control terminals of the RCS will be installed at the following positions:

4.5.1 X-ray inspection system operator position – fully operational.  

4.5.2 Shift supervisor position – display only: status and graphic.

4.6 At the PDR the Contractor will present, for Client approval, all aspects of control system's operation. 
5. Shipment Directing and Monitoring System (SDMS)

5.1 General

5.1.1 The SDMS will be designed to intake incoming shipments, identify the trucks using ALPR and in combination with driver's identification tag to control and route the movement of vehicles in the site area. 

In addition, the SDMS monitors pedestrians: workers and visitors’ access to and in special areas inside the site, as specified.

5.1.2 The SDMS shall be designed to efficiently control the procedures described in Section 3 of this document.

5.1.3 The control systems have the following main tasks:

5.1.3.1 SDMS - Direct and control movement of container/cargo trucks at entry, at all stages of the activity on-site and at exit gate. Control shall be provided with resolution of a single vehicle.

5.1.3.2 Access Control of people into and inside facility areas
5.1.3.3 Managerial control, providing data to correlate with customs data;
5.2 Purpose of the system

5.2.1 Routing and directing the vehicles.

5.2.1.1 The system will include identification and directing means as specified below:

a. Truck ID – based on truck front License Plate Number (TR)

b. Identification tags to be given to the drivers (Inspection/Driver ID)

c. Identification tag reading units to be installed on the site

d. Directing signs, traffic lights, Barriers and other directing aids.
This, in order to allow routing, command and control of all the traffic in the site and throughout the process, from the arrival of the vehicle at the facility gate until its departure.

5.2.1.2 The system will implement directing means as specified below:

a. Dynamic signposts with variable messages according to the directing needs.

b. Traffic lights – as per site design 
c. Barriers and gates
5.2.2 Correlation with Customs data 

5.2.2.1 Purpose of the system:

a. To display the data of the cargo/container's contents at the relevant work stations.

b. To indicate special inspection requirements for the shipment.

c. To define, for operators use, the type of customs required inspection (R / RD/ M / R+M)

5.2.2.2 Cargo data is acquired from the following sources:

a. From customs computer – throughout the unique Inspection Number, defined at the check-in
b. The document scanner.

c. Manual entry at the check-in
5.2.2.3 The contents of the data shall include the relevant information for implementation of the designated inspection: X-ray or/and manual process 

5.2.2.4 It shall be possible to present the screen containing the cargo data at the relevant workstations deployed in the facility (as specified in Sections 3 and 4)
5.2.2.5 The contractor will take into account the need to attribute space in furnishing of the workstations in which system equipment will be installed.

5.3 Components of the SDMS and subsystems
5.3.1 The control system shall include the following components:

5.3.1.1 Access Control subsystem

5.3.1.2 Identification tags – employees (Customs ID) and truck drivers.
5.3.1.3 Readers – LPR, ID cards (both Customs and Driver ID)
5.3.1.4 Cameras (for example: pedestrian wickets, etc)

5.3.1.5 Electronic Signs & Traffic lights
5.3.1.6 Computer system for management and communication;
5.3.1.7 Auxiliary equipment (cables, kits etc.)
5.4 Access Control subsystem - People
5.4.1 Access control system in the site will be based on employees' ID cards and biometric data.
The system shall be deployed at the entrance to some rooms/ areas, mainly sensitive areas as regards of security, safety and/or operational functioning.

5.4.2 Requirements

5.4.2.1 The Contractor shall install Client's approved Access control system at the site’s pedestrians' entrances, buildings’ main entrance and some specific areas/ rooms (TBD at the PDR) 
5.4.2.2 The system shall be based on Card readers & Biometric readers installed close/at the controlled doors/gates

5.4.2.3 System's software package regarding access control and including all the standard functions, for instance: restriction of entry times, restriction of entry sites, prevention of possibility of re-entry, etc. shall be installed at the gate wickets.
5.4.2.4 Access control activity shall not disrupt the operational activity of the traffic routing system.
5.4.2.5 The contractor will install access control equipment at least at the following locations: 

· The entrance to the radiography building 
· The entrance to inspectors’ rooms from the manual search area
· Office building
· Pit area

· Custom's House
· Special areas and rooms (TBD)

·  Communication rooms
5.4.2.6 In addition to control equipment every entry and exit lane (cars and/or trucks) will include:

·    Arm barrier
·    Intercom

5.5 Readers

5.5.1 General

5.5.1.1 Readers, part of SDMS system, shall be installed in the following locations.

a. Private car & Pedestrians site entry/exit lanes
· Pedestrian entrances - Employee card reader

· LPR – Entry & Exit lanes for authorized private vehicles

b. Trucks Check-in & checkout area, next to the entrance and exit cabins

· LPR – acquire the LPN of check-in trucks at the entry lanes
· LPR – acquire the LPN of check-out trucks at the lanes (automatic exit) 

· Driver's Tag reader – truck exit lanes (for backup and receipt)
c. X-ray inspection building 
· LPR - Entrance to X-ray inspection tunnel
· Driver's Tag reader – receptionist/operator's workstation

· Access control at entrance doors to control room, offices and classified rooms (about 12, locations: TBD) - Employee card reader.

d. Manual inspection installation 

· Driver’s tag reader - At inspector's office (re-check workstation)

· Driver’s tag reader - At the inspection pit office
· Driver’s tag reader - At drivers waiting rooms 

· Access control at entrance doors to control room, offices and classified rooms - Employee card reader (about 12, locations: TBD)

e. Customs House 

· Access control at entrance doors to offices and classified rooms - Employee card reader (about 12, locations: TBD)

5.5.1.2 The LPR readers shall be installed in places which will not affect movement of the vehicles.

5.5.1.3 The reader equipment shall be designed for outdoor installation and their operation will not be affected by environmental conditions (IP67 standard).

5.5.1.4 The readers will be installed with a level of resolution allowing continuity of command, supervision and control in all areas of the site.

5.5.1.5 The readers of identification tags, either Driver's tag or employee's ID card: direct access of the card holder is required.
5.5.1.6 The readers for identification of vehicles, Trucks & Private cars, (ALPR) will be able to read the front license plate number of a moving vehicle (position indifferent)
5.5.2 Card Reader & Biometric (access control)

5.5.2.1 The card reader will meet the following requirements:

5.5.2.1.1 There will be indicator lights at the entrance showing “Authorized” or “Rejected”.

5.5.2.1.2 A buzzer will sound to give an audible indication for “Rejected”.

5.5.2.1.3 The lifespan of a reader should be at least 2,000,000 movements.

5.5.2.1.4 Minimum working temperature range 0°C - +50°C.

5.5.2.1.5 In the event of a failure in communication or in the system server, the card/biometric readers must work completely autonomously (using a local controller), and without any interruption to the entry and control of users.  When the communication returns to a normal state, the system tables shall be updated immediately.

5.5.2.1.6 The reader will work using power supplied by the buildings controller.

5.5.2.1.7 The readers shall be protected by a tamper proof switch so that disassembly of the reader will cause an alarm in the system.

5.5.2.2 Every readers/controller shall transmit indications to the system server as follows:

5.5.2.2.1 Authorized gate entry;
5.5.2.2.2 Manual gate entry (by the internal button);
5.5.2.2.3 Attempt to disassemble the reader/server;
5.5.2.2.4 Communication error;
5.5.2.3 Readers designated for multi-use will include function buttons and an alpha numeric keypad.

5.5.2.4 Mechanical characteristics;
5.5.2.4.1 The fitting of the card/biometric readers within the facility will be of the anti-vandal indoor type, suitable for the environmental conditions within the building.  Installation of a reader outside the building will be within outdoor weather-proof anti-vandal fittings and must meet both UL-294 and CE standards.

5.5.3 Truck Driver's ID Tag
5.5.3.1 Driver tag, given as part of the check-in procedure, will be made of rigid paper, locally obtainable. 

5.5.3.2 The tag will contain the following information:

a. Inspection/Truck ID (Monovalent inspection number) - human and machine readable

b. Date/Time

c. Truck next destination

d. Designated parking lane number

5.5.3.3 Driver identification tag will be a bar code (or similar) type.

5.5.3.4 The identification tags will be prepared at the check-in workstation after acceptance of the shipment has been authorized. The tags shall be for one-time use and monovalent for each shipment/inspection.

5.5.3.5 Functioning of the tags shall not be affected by weather conditions (rain, wind, etc)
5.5.3.6 When the truck exits the site, the identification tag will be (preferably) swallowed at the exit gate or put in a special device. 

5.5.4 Licence Plate Recognition (LPR / ALPR)

5.5.4.1 General


Monitoring container traffic into/at and out of the site is based on identifying trucks license plate number at the required locations.

5.5.4.2 Operation

5.5.4.2.1 The system shall acquire and recognize license plate number of private cars and trucks. 

5.5.4.2.2 The LPR systems (about 12) will be installed at the following locations:

· Entrance and Exit lanes for private cars (A few locations according to final site plan and Customs House location) 

· Up to six (6) Entrances lanes at trucks check-in areas.

· Up to six (6) Entrances lanes at trucks check-out areas.

· Two (2) Entrances to the radiation tunnel 

5.5.4.2.3 Private cars - The system will recognize car license plate and will compare it against files of authorized and unauthorized vehicles.

5.5.4.2.4 Reading of the vehicle's license plate shall be of the vehicle's front license plate. 
5.5.4.2.5 It should be noted that location of truck's license plate varies from one truck to other and may be located at the front of driver cabin.
5.5.4.2.6 Each lane will include two (2) IR cameras with IR illuminators.

5.5.4.2.7 The system shall acquire more than one image to insure reliable reading of car license plate.

5.5.4.2.8 Dedicated software shall be supplied with the system.

5.5.4.2.9 Response time of vehicle's license plate recognition will not exceed 3 second.

5.5.4.2.10 Detection wire loop in the asphalt (to supply trigger for camera operation) is required.
5.5.4.2.11 Technical requirements:

· Road width: at least 4 meters.

· Operation distance: up to 15 meters from the vehicle.

· Vehicle speed: 0-80 km/h.

· The system will have al least 4 dry contacts for external equipment operation.

5.5.5 Electronic signs 

5.5.5.1 The electronic Sign, LED variable message sign displays shall be installed in the following locations:

5.5.5.1.1 At the pre-radiography Parking Lot
5.5.5.1.2 At the pre-clearance parking lot (post radiography)

5.5.5.1.3 At the Manual site at the following locations:
5.5.5.1.3.1 Inspection area, near inspectors’ room

5.5.5.1.3.2 Drivers waiting rooms 
5.5.5.2 The outdoor sign shall be sunlight readable, large characters and the viewing angle adjusted so that they can be clearly visible to all drivers.

5.5.5.3 Technical Specifications:
5.5.5.3.1 Display Type: HRSBSC3280, Hi Res. Sun Blazer.

5.5.5.3.2 LED's per Pixel: 1.
5.5.5.3.3 Color: Amber.
5.5.5.3.4 Pixel Matrix (H x W): 32 X 80. 
5.5.5.3.5 Pixel Size: 0.51 cm.
5.5.5.3.6 Pixel Pitch: 2.29 cm
5.5.5.3.7 Active Display Area: 73.1 cm X 182.8 cm (approx.).
5.6 SDMS Computer system 
5.6.1 Requirements
5.6.1.1 The system software will be user-friendly and will allow rapid access to every function.

5.6.1.2 It's preferred that the user interface display will be in Hebrew. 

5.6.1.3 Access to the system functions will be by authorization (password).
5.6.1.4 The system will be able to alert on mistakes/errors in reading identification tags.

5.6.1.5 Communications with other computers will be rapid and will not affect operation of the system in the various work modes.

5.6.1.6 The system will alert on attempts at unauthorized tampering and/or handling of card readers.

5.6.1.7 The system will be planned with a capability for 100% expansion.

5.6.1.8 The system will operate in integration with other systems
5.6.2 SDMS display
5.6.2.1 The SDMS is a tool to manage, monitor and control vehicles in the facility. 
5.6.2.2 The system software has to meet all the above requirements.

5.6.2.3 The interactive map shall display the lists of trucks currently located at site's areas, for example: pre-radiography parking, the radiography tunnel, pre-clearance parking, manual area, pit, exit cabin. The list shall be created based on the recorded outputs of the SDMS detectors/equipment located at the various areas and system's interface with the radiography software. 
5.6.2.4 At the SDMS design Review, the Contractor shall present, for Client's approval, the proposed configuration and specific parameters of the SDMS display, including reference to the following:
5.6.2.4.1  Status of each truck in the site - shown dynamically on-site map background
5.6.2.4.2 Trucks status will be displayable to the authorized system operators using SDMS workstations, using trucks ID numbers:

5.6.2.4.2.1  The monovalent, sequential “Truck ID” number (provided by the SDMS)
5.6.2.4.2.2 Truck LPR
5.6.2.5 Notification to the drivers regarding their next destination shall be performed using the Variable Message Sign (VMS) via the SDMS Server’s internal queues. 
5.6.3 SDMS Reports

5.6.3.1 The supplied system shall include reports generator for the SDMS system.
5.6.3.2 The report generator shall provide a variety of reports, including statistical evaluation regarding:
· All events (inspections) for a particular date or during a defined period; (for example: time at site from entry to exit, Number of inspections, etc)
· All events related to a specific system or subject (Radiography/Manual, etc) defined in the system on specific dates or period
· All events of a particular category 
· All the activity and planning at the system on specific dates;
5.6.3.3 All site events shall be saved in the memory.

5.6.3.4 Final configuration and search capabilities shall be defined at the design reviews and approved by the Customer.

5.6.3.5 The contractor shall supply a suitable software program for producing history reports from the system, including all the relevant licenses.
5.7 SDMS workstations
5.7.1 The SDMS workstations shall be installed in the following locations.

a. Check-in cabin   

b. Check- out cabin
c. Radiography operator/receptionist (x-ray building) 

d. Radiography shift supervisor 

e. Inspectors office (Manual building)
f. Pit inspector’s office (Manual building)
g. Manual supervisor’s offices (Manual building)

h. Site manager (Manual building)
i. Other offices (TBD, up to 5 additional workstations).
5.7.2 Specific authorization levels regarding re-routing of trucks, changing their status or destination shall be defined for each workstation/operator at the DR.
5.7.3 The SDMS system will integrate with the customs system, so preliminary data of trucks that will be invited to the radiography procedure will enter to the existing que of the specific date and time of the invitation. All data from the customs system will be automatically obtained by the SDMS system.
5.7.3.1 The system will allow reserving a truck to a specific radiography tunnel.

5.7.3.2  The system will allow manually “closing” (Not directing trucks) a specific radiography tunnel in case of a malfunction or maintenance.
6. OCR truck gate systems
6.1 General
6.1.1 The contractor will supply all equipment (components as described below) and hardware for the complete installation of this system (LPR, cameras, electronic signs etc.).

6.1.2 The OCR will be designed to intake incoming trucks, identify the trucks container number using OCR (Optical Character Recognition) camera and in combination with SDMS and FCS data make sure that the data at the check-in of the truck’s license plate match the container number. 
6.1.3 The OCR will give an additional approval for the truck clearance at the check-out gate. 
6.1.3.1 The system will include identification means as specified below:

e. OCR camera/s in order to identify the container number.

f. Truck gate (Construction for the cameras).

g. Directing signs, traffic lights, Barriers and other aids.
h. Integration to the SDMS & FCS.
6.2 Components of the OCR system
6.2.1 The OCR system shall include the following components:

6.2.1.1 Cameras.

6.2.1.2 Indication element (Electromagnetic loop or similar).
6.2.1.3 Electronic Signs & Traffic lights

6.2.1.4 Computer system for management and communication.

6.2.1.5 Truck gate (Construction for the cameras).

6.2.1.6 Auxiliary equipment (cables, kits etc.)
6.2.2 Optical Character recognition (OCR)

6.2.2.1 General


The system shall acquire and recognize container’s number. 

6.2.2.1.1 The OCR systems (about 4) will be installed at the following locations:

· Check-in stations at the entrance gates.
· Check-out stations at the exit gates.

6.2.2.1.2 It should be noted that location of truck's container varies from one truck to another.
6.2.2.1.3 Each lane will include at least two (2) IR cameras with IR illuminators.

6.2.2.1.4 The system shall acquire more than one image to insure reliable reading of the container number.

6.2.2.1.5 Dedicated software shall be supplied with the system.

6.2.2.1.6 Detection wire loop in the asphalt (to supply trigger for camera operation) is required.
6.2.2.1.7 Technical requirements:

· Road width: at least 4 meters.

· Operation distance: up to 15 meters from the truck.

· Vehicle speed: 0-80 km/h.

· The system will have al least 4 dry contacts for external equipment operation.

6.2.3 Electric signs 

6.2.3.1.1.1 On the OCR gate in order to indicate the driver whether the container number was read sufficiently. 
6.2.3.2 The outdoor sign shall be sunlight readable, large characters and the viewing angle adjusted so that they can be clearly visible to all drivers.

6.2.3.3 Technical Specifications:
6.2.3.3.1 Display Type: HRSBSC3280, Hi Res. Sun Blazer.

6.2.3.3.2 LED's per Pixel: 1.

6.2.3.3.3 Color: Amber.

6.2.3.3.4 Pixel Matrix (H x W): 32 X 80. 

6.2.3.3.5 Pixel Size: 0.51 cm.

6.2.3.3.6 Pixel Pitch: 2.29 cm

6.2.3.3.7 Active Display Area: 73.1 cm X 182.8 cm (approx.).
6.3 OCR Computer system 

6.3.1 Requirements

6.3.1.1 The system software will be user-friendly and will allow rapid access to every function.

6.3.1.2 It's preferred that the user interface display will be in Hebrew. 

6.3.1.3 Access to the system functions will be by authorization (password).

6.3.1.4 The system will be able to alert on mistakes/errors in reading containers numbers.

6.3.1.5 Communications with other computers will be rapid and will not affect operation of the system in the various work modes.

6.3.1.6 The system will be planned with a capability for 100% expansion.

6.3.1.7 The system will operate in integration with other systems.
6.3.1.8 The supplied system shall include reports generator for the OCR system.

6.3.1.9 All site events shall be saved in the memory.

6.3.1.10 Final configuration and search capabilities shall be defined at the design reviews and approved by the Customer.

6.3.1.11 The contractor shall supply a suitable software program for producing history reports from the system, including all the relevant licenses.
7. Parking control system
7.1 General
7.1.1 The parking control system will give indication regarding the availability of the ramps in the manual check-up stations. 
7.1.2 The system will be comprised from parking control software, vehicle detection sensors and overhead indicators (red/green LED lights). 

7.2 The software

7.2.1 The system will have the ability to be installed as a stand-alone system or in a client server environment whereby multiple users can log in across a network and depending on their access level. 

7.2.2 The system will be a fully soft configurable and allow future system expansion, such as the addition of more ramps, sensors, as well as the addition of entire new parking areas. 

7.3 User interface

7.3.1 The system will support the display of information as Map Displays. 

7.3.2 The map display shall include the capability for showing levels of parking availability. 

7.3.3 The Map view should be an accurate real time representation of the parking area. Each ramp should have a colour indicator which represent in real time the status of the sensor monitoring that’s specific ramp in the facility.

7.3.4 All bay sensor states will be capable of being shown real time on the user interface in the appropriate colour. This will include a sensor failure being depicted as a gray dot in the respective bay on the user interface. 

7.4 Alarms 

7.4.1 Alarms shall have the ability to notify users if the system is not operating properly when the status is measured.

7.5 Sensors 

7.5.1 Each sensor will be mounted centrally above the ramp and have an integrated LED status indicator. 

7.5.2 Sensors shall be hardwired back to a central controller.

7.5.3 Each sensor must be given a unique address or identifying number in a specific zone, so that both the Data concentrator as well as the central control software can identify it and its position. 

7.5.4 Sensor LED Status indicators will be visible through 360 degrees. 

7.5.5 The LED indicators that are to be located above each Bay shall operate in accordance with a truth table driven by the status of the ramp, as follows: GREEN: Vacant RED: Occupied.

7.5.6 Each sensor will be capable of running in stand-alone mode, whereby if it hasn’t had communication from the Zone Controller for a predefined interval, it will operate in Red / Green mode independently until such communication is restored.

7.5.7 Zone Controller 

7.5.8 The manual check-up ramps will be divided into Zone’s. Each zone will have a zone controller that is linked to all the sensors in that zone. 

7.5.9 The Zone Controller will communicate real-time with all the sensors in that zone. The zone controller will poll each sensor individually for its current state and be able to report this state, including sensor failure to the Central Control system when it in turn is polled. 

7.5.10 Each zone controller will have as a minimum, 1 Ethernet port and 2 RS232 ports to enable communication with the central control system.

7.5.11  Each Zone Controller will be capable of being programmed with a unique IP address and its associated gateways and subnet masks. 

7.5.12 Each zone Controller will be polled real time for the central control system and will report current sensor status as well as any sensor failures which have occurred. 

7.5.13 The zone controller will be capable of running test patterns on every sensor connected to it, to assist with the installation, calibration and maintenance of the system.

8. Security & CCTV Systems
8.1 General

8.1.1 The security system shall be implemented following the requirements and descriptions in this chapter.

8.1.2 The security and CCTV system shall comprise of the following main subsystems:
a. C.C.T.V cameras in the radiography tunnel (radiation safety operation).
b. C.C.T.V cameras in the site at specific locations (operational reason)

c. PTZ cameras inside the site

d. Alarm system and detectors
e. Active fence detectors
f. Security Command & Control system (C&C) to control and operate the alarm and C.C.T.V systems
8.1.3 Full integration between the alarm systems and the C.C.T.V system is required, i.e. when alarm occurs an automatic display of the relevant cameras occurs in the control room, including an automatic preset to relevant PTZ cameras.

8.1.4 Site gates 
8.1.4.1 At all site's gates detectors will be installed. 
8.1.4.2 It will be possible to neutralize these detectors during day time.   

8.1.4.3 Lighting system shall be installed for night time operation.

8.1.5 Security events in the site have priority over operational events.

8.1.6 Security Command and Control workstations shall be located at the following rooms:

8.1.6.1 Supervisors (at least 3) rooms in Manual Building - Main
8.1.6.2 Customs House (TBD)

8.1.6.3 Command and control workstation in the gate cabin - Secondary
8.1.6.4 Preparation of Communication infrastructures for Command and Control workstation in the shelter room (Manual Building) – Emergency.

8.1.7 All the Security, Access control & CCTV components will be backed up by a UPS system with 1-hour backup time.
8.2 CCTV System
8.2.1 General

8.2.1.1 The C.C.T.V system will be based on IP technology and will meet all customer IT security requirements.
8.2.1.2 A physical separate network will be used for cameras and all security devices and components.

8.2.1.3 Recording

a. Recording will be 24/7.

b. Storage time - as defined in the table below (6.2.2)
c. Recording quality: high resolution (at least 4MP), 25-30 fps.

8.2.1.4 Full integration between the alarm system and C.C.T.V system is required.

8.2.1.5 The control system shall be integrated with the security C.C.T.V system in order to give possibilities of viewing and extended command.

8.2.1.6 The attach diagram presents the system principals.

8.2.1.7 C.C.T.V system workstations, display and operation shall be installed at:

a. Radiography shift supervisor
b. Radiography operator (display of Radiography tunnel fixed cameras only)
c. Manual area Inspectors supervisors
d. Manual area shift supervisors

e. Site manager (Manual Building)
f. Customs House (TBD)
8.2.1.8 Priority  
a. Priority of using the system (PTZ camera) is according to the order in the previous paragraph.
b. The security has the highest priority (Above all).

8.2.1.9 Final configuration including each workstation’s location will be approved at the design review meetings.

8.2.1.10 Technical requirements from the main devices are detailed below.
8.2.2 Fixed cameras will be installed along the entire perimeter of the fence.
8.2.3 All cameras will be color cameras and suitable for outdoor conditions (temperature / humidity / lighting / protected / protected burglary – IP67 anti vandal). The cameras will have and day and night modes.

8.2.4 PTZ cameras will be installed throughout the site. The resolution of these cameras will be so that will be capable of identifying the number on the containers and vehicle numbers, including the entrance gates /trucks waiting areas, entry and exit from the radiography tunnel.
8.2.5 The resolution of cameras will be determined according to the area analysis and cover required to cover the entire area of ​​the site (by the security supervisor).
8.2.6 The cameras will cover all public areas such as:
8.2.6.1 Parking spaces for private cars and trucks.
8.2.6.2 Waiting area for the radiography tunnel and waiting area post-radiography.
8.2.6.3 Manual check-up ramps.
8.2.6.4 Entrance and exit gates.
8.2.6.5 “Locker" – where confiscated goods are stored.
8.2.6.6 Additional locations that will be defined by the security officer in detailed design stage.
8.2.7 The PTZ cameras will be programmed so they will have fixed directions, programmed for automatic scans and returned to a fixed view after a specified period of time.
8.2.8 In the buildings cameras will be located in sensitive and exceptional areas, such as: entry to the control room, weapons room, executive floor lobby, lobby of each floor, server rooms, and other designated rooms.
8.2.9 Fixed cameras will be installed on the ramps. One camera for two ramps. The cameras will be high resolution (at least 5MP) and will have the ability to effectively identify actions that are carried out inside the containers. 
8.2.10 The contractor will install LED lighting at each of the inspection ramps. The LED will produce lighting at the ramp and in the interior of the containers and will be suitable for the camera’s optimal function.
8.2.11 Control of the entire CCTV system will be carried out through the control room & C&C system, and any other place as required by the security officer (Radiology, Security and any other required places).
8.2.12 At the entrance and exit gates, fixed security cameras will be installed to identify incoming and outgoing vehicles. The cameras will be able to recorded the vehicles identification plate number.
8.2.13 All cameras will be recorded in the NVR system. The NVR will hold the data for at least 90 days. The NVR will have the ability to export data to an external storage (CD, external disk etc.). Downloading the data from the system will not exceed 10 minutes (no matter what file size is being downloaded). The system will be able to download the data as a complete file without segments. The recording system will be placed in a security server room or according to the security officer instructions.
8.2.14 All CCTV system elements (fixed and PTZ cameras, NVR, encoders etc.) will be connected to a UPS system for at least 12 hours.
8.2.15 Area of coverage

The C.C.T.V system will provide area coverage and storage time as follows:

	Serial No.
	Name/Description
	level of coverage
	Storage Time (days)
	Remarks/ Detection capability

	1
	Entry/Exit gates complex (inside and out)
	100%
	90
	Ability to Identify truck's /vehicle LPR 

	2
	Entry check-in cabins area
	100%
	90
	Ability to identify general activities in the covered area

	3
	Pre-radiography parking lot
	80%
	30
	Ability to identify general activities /movements in the covered area

	4
	Access roads/ routes, parking lots "throughout the facility"
	80%
	30
	- refers to trucks

- General activities in the area

loaded/empty

	5
	X-ray inspection building
	100%
	10
	The entire X-ray inspection process. 
Ability to identify presence and any movement of any person in the tunnel (including driver's cabin and all area all around the parking truck, shielding doors, etc.)

	
	Entrance to tunnel (before and after entrance doors)
	
	10
	

	
	X-ray tunnel
	
	10
	

	
	Exit from tunnel (before and after exit doors)
	
	10
	

	
	Truck driver cabin
	
	10
	

	6
	Pre-clearance parking lot (waiting truck)
	80%
	30
	Ability to identify general activities /movements in the covered area

	7
	Manual inspection shed
	100%
	180
	Cameras-PTZ

Including unloading area

- ability to see into each one of  the containers during unloading
Ability to identify general activities /movements in the covered area

	8
	Manual inspection storage area
	100%
	180
	Ability to identify general activities /movements in the covered area

	11
	Offices
	TBD
	60
	Special areas that will be defined with the client


* Remark:  The coverage will be carried out using PTZ commanded cameras and/or fixed cameras as determined by the planner and approved by the customer at the DR.
**Remark:  The contractor will include a POC (pilot) for each IP camera model.
8.3 Perimeter/ Fence Alarm System
8.3.1 The fence will have built-in canals for power cables, network cables, etc. (for cameras, lighting, intrusion detection, access control, etc.). the canals will be separated for each system and marked accordingly. The canals will have future redundancy for expansion of at least 200% tension.
8.3.2 Indicative detectors will be installed along the fence with 100% coverage. The system will have the ability to adjust the sensitivity of each detector.
8.3.3 The Alert System will be based on three-axis electronic oscillatory signal detectors that will provide an alert when attempting to penetrate the protected site and will combine video from peripheral cameras to the alarmed area.
8.3.4 The indications/ alarms from the fence will be transferred to the C&C and control room (and to any other place designated by the security officer) automatically in case of an alarm. The indication will be transferred in two ways: voice indication & visual indication. The visual indication will from the fixed and PTZ cameras that cover the alarmed area.
8.3.5 The fence alarm system will enable the disconnecting of certain fence segments from alarms, or alternatively to allow higher / lower sensitivity, as well as the option to operate the system in day / night mode according to the customer's request. The system will enable the modification of various parameters in each detector in order to receive alarm from a single detector or a group of detectors.
8.3.6 The system will allow for programming and redefining as necessary, for example: signal sensitivity, alarm volume, day / night settings, system / part of the system setup (if required).
8.4 Access Control

8.4.1 All entrances to the compound, buildings entrances, designated areas and offices will be connected to an access control system that will connect to the C&C and control room.
8.4.2 Access to these areas will be authorized by a biometric reader / customs proximity card that is with accordance to the customs cards protocol.
8.4.3 The system will alert in case of open doors/areas by means of a loudspeaker and / or local buzzer on the doors / gates that are monitored. The system will provide a visual alert in the C&C system.
8.4.4 The system will allow definition of groups and/or individual permissions as required.
8.4.5 The system will alert of unusual events such as unauthorized access to different areas, expired card, blocked card, etc.
8.4.6 The system data will be stored data of at least 1 year, and the system will allow the data to be exported to the Word / Excel file, as needed by authorized personal.
8.4.7 The system will be connected to the fire alarm system in order to release locks in case of emergency. 

8.4.8 All site’s regular visitors will have a permanent badge that will be issued by the site's administrators and will confirm their access to certain areas of the site.

8.4.9 The card issuing system will issue RFID cards that are encoded with information that will be provided by the access control system.
8.4.10 The contractor will provide and issue 10,000 cards.

8.4.11 The system will be located in a designated office and the approach to issuing a new card will be carried out using a user name and password for holders of positions only.

8.4.12 The RFID cards will include the card holder name and picture. 
8.4.13 The readers for pedestrians and private vehicles will be able to read the card at a maximum distance of 30 cm. The readers for truck drivers will be installed on flexible arms and will be able to read the driver's card at a distance of at least 1 meter.

8.5 Control room

8.5.1 The control room will be active 24/7.

8.5.2 The room will be located on a high floor in the office building at an isolated location (as much as possible), and that overlooks the site area as much as possible.
8.5.3 The room will be built as a safe room (concrete walls). 
8.5.4 The room will have 2 doors – safe room door and a regular office door. The regular door will be access controlled.
8.5.5 The room will contain electric and data outlets as will be specified by the client at the detailed design phase.
8.5.6 Access to the room will be with a card reader.
8.5.7 A CCTV camera will record the room 24/7.
8.5.8 The room windows will be as wide and large as possible and will conform with the “safe room” Windows standard.
8.5.9 All windows will have shades.
8.5.10 Dedicated screens and computers for each system on site.
8.5.11 Infrastructure for cable/ satellite television.
8.5.12 Designated control room furniture.
8.5.13 The room will have an internal room that will serve as a weapons room. The weapons room will store up to 5 weapons and meets the specifications of the Ministry of interior.
8.5.14 8 LTE/PTT portable radios docking stations.
8.5.15 SMS marketing software. 
8.5.16 The control room will have the following capabilities/ systems/ features:
8.5.16.1 FCS.

8.5.16.2 Command and control system for the management of the site’s security systems.
8.5.16.3 NVR system.
8.5.16.4 NVR/DVR system of the existing site.

8.5.16.5 Access control system.

8.5.16.6 Fire detection system and panel.
8.5.16.7 A dedicated indication panel for distress buttons.
8.5.16.8 PA system.
8.5.16.9 Intrusion detection system (including site map).
8.5.16.10 Intrusion detection system of the existing site (including site map).

8.5.16.11 Fence alarm system.
8.5.16.12 Fence alarm system of the existing site (including site map).
8.5.16.13 Telephony.
8.5.16.14 Air conditioning.
8.5.16.15 Computers.
8.5.16.16 Automatic closures system.
8.5.16.17 Two work stations.
8.5.16.18 Safe for classified documents. 
8.5.16.19 Screens for security cameras, fence control system, electronic closures, and various security systems.
8.5.16.20 All security and low-voltage systems will be backed up to a minimum of 12 hours.
8.5.16.21 Hot / cold water machine stand.
8.5.16.22 Illumination - Adjustable light intensity / dimming.
8.6 Intrusion Detection
8.6.1 Intrusion detection system will be installed in the office, the radiography tunnel, “locker” and storage room.

8.6.2 The system will comply with Israeli standards including Standard 1337. 

8.6.3 The system will have a back-up for at least 48 hours.
8.6.4 The system will be connected to the C&C system.
8.7 Patrol system

8.7.1 Installation of an electronic patrol system.

8.7.2 The detectors will be installed in various locations on the fence and inside the facility according to client detailed design.

8.7.3 The system will include data storage for a minimum of one year including the name of the location of the detector, date of the call, precise location.
8.8 Automatic closures system

8.8.1 Automatic closures system will manage and operate the entrance gates, control room, security manager room.
[image: image1.emf]
9. Technical Requirements for system components
9.1 General

9.1.1 The technical requirements and definitions that appear in this Specification are the minimum required for each system / method separately and all together as a comprehensive system. 
9.1.2 The technical and operational performance of the subsystems and methods shall not deteriorate over the time and shall not be affected by ambient conditions on site.
9.1.3 Contractor's proposal shall include a detailed description of systems components, including technical specification. Final configuration and systems specifications shall be defined and approved at the DR meetings.

9.1.4 All servers/ computers/ hardware will be hardened. The hardening will be done according to the best practice of the manufacturer of the hardware and according to the latest guidelines of the customs information security department.
9.2 HD IP fix camera, day/night 
9.2.1 Color network camera

9.2.2 Color photography in daylight conditions and monochromatic photography in illuminated night-time conditions, including automatic shift between modes.
9.2.3 IR projector for night time.
9.2.4 RJ45 connection to Ethernet 10/100base-T.

9.2.5 CMOS/CCD 1/3" camera sensor.

9.2.6 Progressive scanning.
9.2.7 H-264, MPEG-4 video compression
9.2.8 Protocol: TCP/IP, ICMP, IGMP, DHCP, HTTP, ARP, RTP, RTSP, RTCP, NTP, UDP unicast, UDP multicast

9.2.9 25-30 fps in 3MP resolution.
9.2.10 LUX sensitivity 0.1 in color, 0.5 LUX B&W at least (on F1.4 lens)
9.2.11 SNR (Signal to noise ratio) at least 50 db

9.2.12 Shutter speed 1/1.5 - 1/30,000.

9.2.13 Automatic focus
9.2.14 At least 50 IRE
9.2.15 Dual stream

9.2.16 Dry contact in and out

9.2.17 Ambient conditions: -10(+50(C, 90% humidity.
9.2.18 Must work in outdoor conditions (IP67)
9.2.19 Working voltage: 12/24 VDC Working support on PoE - Power over Ethernet 
9.2.20 Automatic white balance
9.2.21 CS/C mount lens, metal thread.
9.2.22 Cost of the camera includes license.

9.2.23 The supplied camera must be fully compatible and have an interface for working with an NVR to be supplied.

9.2.24 The camera must be made by a well-known manufacturer, preferable a European/ Japanese or US manufacturer.
9.3 Lenses for megapixel camera
9.3.1 The contractor shall supply lenses consistent with the specifications below. The type and direction of the lens will be defined and approved at the time of installation on the site.

9.3.2 Varifocal lens compatible with megapixel cameras.

9.3.3 Compatible with 1/4" sensor or equivalent for 1/3" sensor
9.3.4 Focal length - 3-10 mm. or 5-50 mm

9.3.5 Aperture f/1.6 at least
9.3.6 The lens shall be made of polished glass.

9.3.7 CS/C mounts with metal thread.
9.4 PTZ – day / night IP camera (X36) 
9.4.1 Color network camera

9.4.2 Color photography in daylight conditions and monochromatic photography in illuminated night-time conditions, including automatic shift between modes.

9.4.3 RJ45 connection to Ethernet 10/100base-T.

9.4.4 ¼" or 1/3" CMOS/CCD sensor.

9.4.5 Progressive scanning
9.4.6 H-264, MPEG-4 video compression
9.4.7 Protocol: TCP/IP, ICMP, IGMP, DHCP, HTTP, ARP, RTP, RTSP, RTCP, NTP, UDP unicast, UDP multicast

9.4.8 25-30 fps in 3MP resolution.
9.4.9 LUX sensitivity 0.5 for color, LUX 0.1 for B&W at least (on F1.4 lens)
9.4.10 SNR: at least 50 db.

9.4.11 Automatic aperture 1/1.5-1/30,000
9.4.12 Automatic focus
9.4.13 At least 50 IRE
9.4.14 Dual stream

9.4.15 Dry contact in and out

9.4.16 Ambient conditions: -10(+50(C, 90% humidity.
9.4.17 Must work in outdoor conditions (IP-65)
9.4.18 Working voltage: 220 VAC
9.4.19 Automatic white balance
9.4.20 Horizontal tilt angle: 360(, continuous.
9.4.21 Vertical tilt angle: +30 ( to -80(.
9.4.22 Speed of horizontal tilt: 1-100(/second.  Varies according to operation
9.4.23 Vertical tilt speed: 1-20(/second.  (30(/ second in preset modes), varies according to operation.
9.4.24 3.3-119 mm. optical zoom lens (x 36) at least. Refers to ¼" CCD
9.4.25 Cost of the camera includes license.

9.4.26 The supplied camera must be fully compatible and have an interface for working with an NVR to be supplied.

9.4.27 In the X-ray inspection tunnel, the camera equipment will be protected against radiation disturbances.
9.4.28 The camera must be made by a well-known manufacturer, preferable European, Japanese or US manufacturer.
9.5 NVR recording / operating switching system
9.5.1 General requirements
9.5.1.1 The contractor will supply a CCTV system with switching, routing and recording capabilities. The system to be supplied will include all the necessary components: server, means of storage, screen, keyboard/keypad, operating measures, software, etc.

9.5.1.2 Number of cameras (estimated) - 100
9.5.1.3 The video signal to the system shall be transmitted on IP infrastructure. The communication network for cameras/security shall be a physical separate network.
9.5.1.4 The system software program shall be installed on computers with an up-to-date Windows operating system, shall facilitate real-time video surveillance as well as viewing of archived recordings. Different levels of surveillance will be possible, adapted individually to the end user.

9.5.1.5 All the video cameras will receive, record, store and route pictures to the system screen and/or accompanying screen.

9.5.1.6 The system will facilitate real-time viewing of video sources as well as playback and search simultaneously without any interference between the two activities.

9.5.1.7 A password (authorization) mechanism is required to allow the system administrator to define passwords for different users.

9.5.1.8 The system shall be operated from a client operating station.

9.5.1.9 The system will support the entire range of cameras which are connected to it, including PTZ cameras.

9.5.1.10 The system shall be expandable.

9.5.1.11 The system to be supplied will include all the permits / licenses required for full operation. Including client licenses for 20 operating stations
9.5.2 Technical requirements
9.5.2.1 Archive storage will be based on storage on local disks and shall support storage on NAS/SAN/DAS.

9.5.2.2 The system must support the updated Windows operating system.

9.5.2.3 High-quality recording of color video signals
9.5.2.4 Each server will handle 35 cameras (at most).
9.5.2.5 Continuous, round-the-clock recording (24/7/365) of all information channels 
9.5.2.6 Capability of storing data according to the required periods, as specified in clause 6.2.2. 
9.5.2.7 FIFO-based saving mechanism

9.5.2.8 During a synchronized playback from the archive, the user shall be able to simultaneously operate functions such as Fast Forward, Rewind, and jump to specific time points - so that this procedure occurs simultaneously on the video of the cameras on synchronized playback.

9.5.2.9 Hebrew interface for surveillance and configuration of the system is required.
9.5.2.10 A full back-up of the files must be kept. Category Raid Level 5, recording on N hard drives + back-up drive + system administration drive
9.5.2.11 Video signal recording data:
a. At least 25 frames/second per channel.

b. Megapixel camera recording as defined in this specification based on the camera's maximum speed. 
c. Resolution – at the same level of viewing resolution
d. The system shall have an option for defining at least 3 resolution levels: low, moderate, high (4 CIF).
e. At least 256 shades of gray. 16 million different colors.
9.5.2.12 The system shall be capable of supporting cameras of up to 8 mega pixels.

9.5.2.13 USB and SCSI ports for CD-RW ROM support or RW DVD for copying and backing up files
9.5.2.14 Standard compression - h264
9.5.2.15 The system must support ONVIF for maximum compatibility and flexibility, in favor of interfacing with standard systems in the future.

9.5.2.16 The system must support Dual Stream mode for surveillance and recording of different qualities. This capacity will also facilitate choosing the recording quality which will be saved for a longer period.

9.5.2.17 All the information channels shall be synchronized, including during reproduction.

9.5.2.18 Option to display real-time picture + pre-alarm picture from select cameras
9.5.2.19 Option to watch up to 16 channels simultaneously
9.5.2.20 Each channel shall contain all the information required for locating and identifying it.
9.5.2.21 Common, shared time clock for the entire system
9.5.2.22 Ability to fully operate and control PTZ camera system
9.5.2.23 Option to set up input for each video channel at the following levels:
a. Brightness
b. Contrast
c. Color
9.5.2.24 Input identification – the system shall contain a mechanism for integrating text at each entry with the following features:
a. Option to combine letters and numbers
b. 16 characters per channel
c. Hebrew font (preferable)
d. Option to set dark background
9.5.2.25 Option to save recorded files/ segments for a longer period by downloading to a disk/DVD/USB device.
9.5.2.26 Alarm input for each channel to allow changes in the recording parameters.

9.5.2.27 Outlet connections to the network – the system shall have an outlet that hooks up with the TCP / IP network.

9.5.2.28 The system will contain a password mechanism to prevent an operator from changing the system setup and to prevent unauthorized operators from deleting files.
9.5.3 Operation of the recording system
9.5.3.1 Operation of the recording system, surveillance, file download, etc. shall under no circumstances interfere with the system's recording operation.

9.5.3.2 On-going control and operation of the recording system shall take place from a designated position on the recording system.
9.5.3.3 All system operations will be accompanied by feedback to the operator regarding the nature of the operation he is performing, the on-screen display mechanism, or equivalent.
9.5.3.4 The system's interface should be user friendly and will be operated by means of icons or by operating menus, etc.

9.5.3.5 The operating screen will be based on a map of the site and shall include all elements relevant for icon-based operation, such as: cameras in the area under surveillance, etc.

9.5.3.6 It must be possible to position and place the icons that appear on the screen spatially, as necessary. For example: the icon for a camera in the corridor shall also indicate its filming direction.
9.5.3.7 Each icon will contain its relevant information. Each icon will have an information table with its operating options. The table will contain information such as: name of the camera, its location, filming data, etc. The information table will be operated by right-clicking on the mouse.

9.5.3.8 The operator shall be able to playback files saved on the hard drive at any time without this affecting the recording process. Response time from making the request until the playback commences shall be no more than 3 seconds.
9.5.3.9 The following shall be possible when the video signal is played back:
a. Zoom-in on the picture.
b. Freeze the picture.
c. Fast forward and rewind
d. Control over color, contrast and luminance.
e. Simultaneous display of several synchronized pictures.
9.5.4 Requirements for operation of cameras
9.5.4.1 The system shall control the PTZ cameras and zoom lenses.   
9.5.4.2 Full control of all directions: up, down, left, right.
9.5.4.3 Full control of focus and zoom.
9.5.4.4 Operation by means of a joystick and keyboard.
9.5.4.5 Capable of issuing a command for RS485 cameras or corresponding
9.5.5 Support on VMD and analytics:

9.5.5.1 The system will interface with advanced end products for VMD and analytics, such as IOI, Agent VI, and others. The supplier must present existing interfaces.

9.5.5.2 The system shall facilitate the integration of end equipment for analytics and a concentration of analytic scenarios so as to create events in the system and generate alerts.

9.5.5.3 The terminal operator shall be able to "arm" and "disarm" the analytics mechanism on the terminal equipment via a surveillance program interface.

9.5.5.4 The surveillance interface shall display analytics scenarios in real time, including an option to display the tracking of an object, mark its movement, indicate the trail, etc.
9.5.5.5 The administrator interface shall enable, at least, the following actions:
a. Definition of IP addresses and parameters for cameras, compressors, and de-compressors
b. Definition of parameters for video bandwidth
c. Full management of access authorizations and passwords  

d. Timing of archive storage for each camera

e. Number of days during which video recordings from cameras shall be saved.
f. Duration of storage before and after an event (per camera)
g. Parameters of recorded video data or live data (per camera)
h. Network (multicast communications, multicast communications via server or UDP protocol per camera).
i. Definition of activities based on system events.

j. Definition of photography sites and groups of cameras on the site.
9.5.6 Production
9.5.6.1 The system shall provide the user with all the measures required to retrieve and save files on a disk / DVD, flash drive, external HD etc.
9.5.6.2 The control station shall contain all the equipment (burner, converter, etc.), software and apparatus required for proper operation.
9.5.6.3 The contractor will provide software packages that enable all the files saved on disk to be played on a PC, up to a quantity of 10 units.

9.6 Security Command & Control 
9.6.1 General 

The security systems Command and Control (C&C) system shall coordinate, display, handle and operate the following: 

9.6.1.1 Receive, display and handle alarms from the entire range of detectors and sensors in the system.

9.6.1.2 Control and operate the system's CCTV cameras. 
9.6.1.3 The system will have a set of maps of the site that lay-out all the security elements & equipment (cameras, detectors, readers etc.) and will display any alarmed section in the fence or buildings on these maps.  
9.6.1.4 Be able to operate processes interfacing with the system, consistent with the capability of involving processes, for example:  intercom, activate equipment, access control, etc. 

9.6.1.5 Playback of the CCTV recording system, production of reports according to various cross sections as well as an "event portfolio" producing as per operator's instructions. 

9.6.1.6 The supplied system, including the work stations, shall include all the permits / licenses required for its full operation as well as routine updates as part of the comprehensive service and maintenance.
9.6.1.7 Contractor's proposal shall include a detailed description of the system configuration, including computers and server’s technical specification. Final configuration shall be defined and approved at the DR meetings.
9.6.2 C&C workstation Configuration
9.6.2.1 The computers and systems that require memory must be supported by a UPS system as per the requirements in this specification. 
9.6.2.2 The operating workstations shall be PC based and shall include all designated software programs required for operation, control, maintenance, calibration, etc. only.

9.6.2.3 The workstations shall contain processes and connections (or connections means) for connecting at least 4 screens.  It must be possible to use all the software programs described in this chapter on all the screens.  
9.6.2.4 The designated software programs in the C&C system shall operate through the Windows operating system, in Hebrew.  The contractor's proposal shall specify the proposed programs.

9.6.2.5 The C&C system must be capable of handling and managing at least 20 CCTV displays concurrently. 

9.6.2.6 The supplied computers shall comply with the requirements listed in this specification. The computers shall have internal and external memory components that are adequate for their function and for the number of messages that must be kept in the database.  All data shall be collected using the FIFO method. The computer hardware that is supplied must be the most up-to-date available at the time of supply. 

9.6.2.7 The system printer shall be connected to the system server (directly or via the network). Data or reports shall be printed per request.

9.6.3 System main features and requirements:
9.6.3.1 The C&C software shall include a diagram/aerial photograph/map of the site and be capable of zooming in on the diagrams on a larger, more detailed scale. 
9.6.3.2 Icons shall appear on the diagram clearly describing the systems/processes/equipment installed on site and their status – active and in working order, shut-down, alarm, out of order, etc.

9.6.3.3 It shall be possible to define a detailed treatment process for an alarm /special event in the system, as follows:

a. Definition of which of the system workstations the event will be displayed on.
b. Definition of the chain of response required.

c. Definition of which processes are to be activated (automatically) when an event occurs;
9.6.3.4 When an event occurs, the system shall automatically display pictures/videos that are relevant to that event, including real time pictures/videos from the relevant camera/s and a pre-alarm picture/video, respectively.

9.6.3.5 All text information in the system: Data, menus, operating instructions, help screens, shall be in Hebrew.

9.6.3.6 Each detector's work mode (ready/neutralized) shall be defined separately. The status of each detector shall be clearly displayed on the site map. 

9.6.3.7 Each detector shall have an accompanying text box, mouse activated. The text box shall contain a brief description of the relevant component.

9.6.3.8 The system shall comprise of a main and a secondary workstation. The system shall provide flexibility regarding the definition of display, operation and treatment preferences between the different stations, including definition of which workstations handle a particular event and which workstations are prioritized in activating processes, for example: control of PTZ cameras.

9.6.3.9 When several events must be dealt with simultaneously, the following will be performed:

9.6.3.9.1 The initial alarm automatically zooms-in on a map of the area of the event and displays a line in the table of alerts.

9.6.3.9.2 The alert immediately displays a set of cameras according to the definition.

9.6.3.9.3 The second alarm displays another line in the line of alerts.

9.6.3.9.4 The second alarm generates a display of another set of cameras, provided that there is a free screen/space available for the display.  If there is no available screen/space, generation of the pictures will wait.

9.6.3.10 When the event has been dealt with and a screen/space becomes available to display the cameras, the cameras waiting in line will automatically generate their display.

9.6.4 CCTV operation 

9.6.4.1 Operation shall be simple and user friendly. The operator shall operate the CCTV system from the system screen and main alarm display.
9.6.4.2 Operation shall be by means of icons or operating menus, etc.
9.6.4.3 The operation shall be based on a map of the site and shall include all elements relevant for icon-based operation, such as: cameras in the area under surveillance, alarms, etc.
9.6.5 Interfaces with related systems:
9.6.5.1 Interface with related systems (alarms, CCTV, access control, etc.) shall be based on a detailed protocol between these systems and the C&C system. 

9.6.5.2 Interfacing with the C&C system will facilitate:

a. Automatic generation of a picture depending on the event
b. Full operation of the CCTV system as described in this chapter. 

c. Full investigation of the recordings database
d. An option to download/ copy (burn) files.

9.6.6 Indication, operation and control 
9.6.6.1 At Systems Design Review the Contractor shall present for Client approval system's configuration, specifically referring to the following items: 
9.6.6.1.1 Display and basic operation
9.6.6.1.1.1 The system's display shall be based on an aerial photograph / map of the site and shall include indications.  The scale of the site will be emphasized on the drawing and each section will be marked on it separately.  Icons will be defined for the alarm system as well as detectors and processes on the site, and the surveillance zones for the CCTV cameras will also be defined.
9.6.6.1.1.2 All events shall be saved. 

9.6.6.1.1.3 The system shall include reports production 
9.6.6.1.1.4 Sensitivity of the different system sensors/detectors will be adjusted and calibrated from the C&C station.  The system manager (security officer) shall have an access code to perform this action. 

9.6.6.1.2 Indication
a. Audio indication 

b. Visual indication: displayed icon on site's map, changing colors/event status and category, fixed or flashing display, etc. 

c. Close-up capabilities - displaying detailed maps/drawings of alarm area. The contractor shall submit a diagram of the display and the various drawings that appear in the close ups for the client's approval. 

d. Text display

e. The number of messages in the system 
f. The wording of the messages shall be coordinated with and approved by the client. 
9.6.6.1.3 Operation method (icons, mouse, keys, etc)
9.6.6.1.4 Alarm mode operation 
9.6.6.1.5 Indication and operation in frequent malfunction situations
9.6.6.1.6 Reports 

The system shall include printed and on-screen reports, referring, at least to: 
· Events on a particular date or during a defined period
· All events from a specific system or section/zone or from several sections/zones defined in the system on specific dates.
· All events of a particular category – such as all the alarms, all the OFF/ON messages, etc. (on specific dates) 
· All the activity and programming at the control center on specific dates.
· Shift between day/night modes. 

Final configuration shall be defined at the DR.
9.6.6.1.7 Access Control


The system shall have several safety access levels that allow/disable various operations and programming, consistent with the user's security level and function:
a. Level 1 – operator level 

b. Level 2 – superior's level.
c. Level 3 – technician level.
d. Level 4 – manager's level, security officer.
Each level operations shall be defined at the DR meetings.
9.6.7 Client Computer configuration 
9.6.7.1 Contractor's supplied computer/server shall be adequate to fulfill the operational requirements of the system. The proposed configuration shall be presented for approval at the DR meeting.

9.6.7.2 Following is the minimal basic configuration (for reference only):
9.6.7.2.1 Dell XPS Tower or equal
9.6.7.2.2 Processor: Intel® Core™ i5-7400 Processor (6M Cache, up to 3.5 GHz)
9.6.7.2.3 Memory: 8GB, 2400MHz, DDR4.
9.6.7.2.4  1TB 7200 rpm Hard Drive
9.6.7.2.5 Video card: NVIDIA® GeForce® GT 1030 with 2GB GDDR5 Graphics Memory or equal.
9.6.7.2.6 The chassis shall contain an integral sound card.
9.6.7.2.7 USB ports.

9.6.7.2.8 Optical drive: DVD-RW Drive (Reads and Writes to DVD/CD).
9.6.7.2.9 The chassis must be safe and fitted with an extra fan in addition to the one supplied by the manufacturer.  The case and supplier must appear on Intel's recommended list. 
9.6.7.2.10 Hebrew/English engraved keyboard with 104 keys (known brand) connected without an adaptor.  

9.6.7.2.11 Mouse, including literature, drivers, and a mouse pad.

9.6.7.3 WIN 7 operating system, 64 BIT.
9.6.8 The contractor shall undertake to install revised versions of the alarm system for at least 7 years from receipt of the system

9.7 Security requirements for computer systems
9.7.1 The security systems for the site and control rooms will be administered using a domain controller (DC) server and backup server, which include a Windows updated operating system, including client licenses for all the computers.  

9.7.2 The security system will include the following modules:

9.7.2.1 Applications control module, for applications approved by the system administrator.  

9.7.2.2 Device control module for integral and portable devices
9.7.3 Basic requirements for the applications control module:

9.7.3.1 Only approved applications may be used.

9.7.3.2 Option for fast access to applications, without the need to reboot the computer or exit the system.

9.7.3.3 Ability to change access authorizations on the spot.

9.7.3.4 Ability to copy a current list of authorizations onto external magnetic media for backup and continuous protection. 

9.7.3.5 Ability to keep a record of and document user requests to operate approved and non-approved applications.

9.7.3.6 System administrator activity must be recorded and documented.

9.7.3.7 Ability to establish a standard system response if a non-approved application is used - operation or blocking. 

9.7.4 Requirements in principle for the device control module:

9.7.4.1 The operating system shall be protected by means of an access control system which restricts user access to devices and system components. 

9.7.4.2 The system must provide protection against viruses, Trojan horses, worms, and unknown monitoring programs (illegal or unauthorized) in the system.
9.7.4.3 The system will provide command and control over the transfer of data to devices authorized by the system administrator by receipt of a copied file name or full copy of that file when memory content is copied.

9.7.4.4 Following is a description of the key properties and specifications required:

a. Ability to manage a list of authorizations (passwords) for each user and group of users
b. Ability to define special passwords for a specific computer or device
c. Prevent use of unauthorized devices and those with which the system is unfamiliar.

d. Ability to use approved devices for operation only.

e. The system should be able to provide a special ID number for each device.

f. Ability to provide access, reading and/or writing.

g. Ability to time access to a particular device in advance and for a given time.

h.  Ability to provide temporary access to a specific device.

i. Ability to create a library of DVDs/CDs and passwords for users or groups of users.

j. Ability to create lists of portable media with special ID numbers and user passwords.

k. Option for each user to use portable media by means of encrypted systems.

l. Update list of authorized file signatures for each log-in to the system.

m. Ability to change access authorizations immediately.

n. Ability to backup the current list of passwords on a desktop or laptop which is not connected to the network, thus providing continuous protection. The file will be updated when the computer is reconnected to the network.

o. Ability to limit the quantity of data which is copied from a particular computer (or network) onto a PSD (portable media or disk).

p. Support is to be provided for the following devices:

· Hard drives

· Biometric devices
· Modems

· Wireless network cards

· Digital cameras

· DVD/CD burners/players

· Scanners

· Flash drives

· USB printers

q. Support is to be provided for the following devices:

· USB

· LPT

· Fire Wire
· IrDA

· PCMCIA

· COM 

· IDE 

· S-ATA

9.7.5 Security System Server– minimum configuration:

9.7.5.1 The server will be HP DL 360G9 or equal.

9.7.5.2 Processor Core: at least 10
9.7.5.3 Processor Cache: L3 Cache – 25MB 
9.7.5.4 Processor speed: 3.1 GHz

9.7.5.5 Memory Type: DDR4 Registered (RDIMM) or Load Reduced (LRDIMM)
9.7.6 Security system WS - Minimal Configuration
9.7.6.1.1 Dell XPS Tower or equal
9.7.6.1.2 Processor: Intel® Core™ i5-7400 Processor (6M Cache, up to 3.5 GHz)
9.7.6.1.3 Memory: 8GB, 2400MHz, DDR4.
9.7.6.1.4  1TB 7200 rpm Hard Drive
9.7.6.2 Network card 10/100/1000
9.7.6.3 4 USB ports.
9.7.6.4 DVD SATA burner at least.

9.7.6.4.1 Optical drive: DVD-RW Drive (Reads and Writes to DVD/CD).
9.7.6.5 The chassis must be safe and fitted with an extra fan in addition to the one supplied by the manufacturer. The case and supplier must appear on Intel's recommended list.

9.7.6.6 Hebrew/English engraved keyboard with 104 keys (known brand) connected without an adaptor.
9.7.6.7 ATI or NVIDIA GeForce 1 GB screen card, including HDMI connector;
9.7.6.8 WIN 7 operating system, 64 BIT.
9.7.6.9 The contractor shall install the updated versions of the system software, for at least 7 years from system acceptance. Upgrading of the versions is part of the comprehensive service and maintenance contract.

Note: Contractor's proposed configuration will be examined for approval or a revised version will be supplied in coordination with the contractor.

9.8 Access control system (ACS).

9.8.1 An ACS shall be provided to ensure that access to the site, important, sensitive or non-public areas is limited to those that have the authority to enter.
9.8.2 The system will integrate with the existing system installed on site.
9.8.3 Estimate number of controlled doors – 50.  An exact amount and locations to be fixed in the DR.
9.8.4 Access by authorized personal shall be by cards and photo ID.

9.8.5 The system shall provide additional security by enforcing time rules, raising alarms in the event of an unauthorized attempt to gain access, and by recording all access movements, in and out, for analysis in the event of later discovery of a security breach. The system shall include the provision to issue new ID cards and register them on the ACS data base as well as to delete cards that have been stolen or lost.

9.8.6 The system shall be with the following basic features:

9.8.6.1 Fully configurable access security levels, time zones and door groups thus enabling the system to be configured to control that has access to which area and during what time periods they may gain access to those areas.

9.8.6.2 The system shall be designed to manage a minimum of 60 doors or gates and 10,000 users.

9.8.7 The system shall incorporate a number of additional features including:

9.8.7.1 Reading in and out of staff at all perimeter access points and/or other designated access positions.

9.8.7.2 Anti-tailgating to prevent persons failing to individually request/register access.

9.8.7.3 Anti Pass Back.

9.8.7.4 Invalid access card detection.

9.8.7.5 Insecure door/forced alarm indication, both remotely and at the controlled door.

9.8.8 Access control Card (with Picture).

Default: Customs employee’s card. 

For use of additional authorized personnel note the following: 
9.8.8.1 RFID
9.8.8.2 Works with proximity technology
9.8.8.3 Reading distance will be 5 – 100 cm.

9.8.8.4 The card will meet all implemented international standards for cards of this type from the electronic and the durability points of view, the size and the physical data.

9.8.8.5 The card will be a dual card (proximity and magnetic).

9.8.8.6 Material: PVC.

9.8.8.7 Size: 5.4 X 8.67 X 0.084 cm.

9.8.8.8 Without a battery.

9.8.8.9 The lifespan of the card under normal use should be 5 years.

9.8.8.10 The card should be printable using normal Dye Sublimation systems from both the aspect of the magnetic material and the aspect of the edge of the card which must be de-burred.

9.8.8.11 Coding of the card will be done by the customer.  The contractor will supply suitable equipment.

9.8.8.12 The printing on the card will include:

9.8.8.12.1 Customer logo.

9.8.8.12.2 Employee information.

9.8.8.12.3 Photograph.

9.8.8.13 The information contained within the card will include at least:

9.8.8.14 Employee Name.

9.8.8.15 Employee Number.

9.8.8.16 Company Name.

9.8.8.17 Card Number.

9.8.9 Card Reader
9.8.9.1 The Contractor is required to supply, install and deploy proximity readers, RFID.

9.8.9.2 Power supplies for the card readers will be included in the price of the reader.  The reader will be able to read all smart cards that will be in the system.

9.8.9.3 The card reader will meet the following electrical requirements:

9.8.9.3.1 There will be indicator lights at the entrance showing “Authorized” or “Rejected”.

9.8.9.3.2 A buzzer will sound to give an audible indication for “Rejected”.

9.8.9.3.3 The lifespan of a reader should be at least 2,000,000 movements.

9.8.9.3.4 Minimum working temperature range 0°C - +50°C.

9.8.9.3.5 In the event of a failure in communication or in the system server, the card readers must work completely autonomously (using a local controller), and without any interruption to the entry and control of users.  When the communication returns to a normal sate, the system tables must be updated immediately.

9.8.9.3.6 The reader will work using power supplied by the building’s controller.

9.8.9.3.7 The readers will be protected by a tamper proof switch so that disassembly of the reader will cause an alarm in the system.

9.8.9.4 Every reader/building controller will transmit indications to the system server as follows:

9.8.9.4.1 Authorized entry.

9.8.9.4.2 Manual entry (by the internal button).

9.8.9.4.3 Attempt to disassemble the reader/server.

9.8.9.4.4 Communication error.

9.8.9.5 Readers designated for multi-use will include function buttons and an alpha numeric keypad.

9.8.9.6 Mechanical characteristics.

9.8.9.6.1 The fitting of the card readers within the facility will be of the anti-vandal indoor type, suitable for the environmental conditions within the building.  Installation of a reader outside the building will be within outdoor weather-proof anti-vandal fittings and must meet both UL-294 and CE standards.
9.8.10 Biometric Reader.

9.8.10.1 Based on fingerprint recognition.

9.8.10.2 Operate in tow modes

9.8.10.2.1 "One to one" mode.

9.8.10.2.2 "One to many" mode.

9.8.10.2.3 Possibility to switch between the tow modes.

9.8.10.3 Optical recognition – 500 DPI.

9.8.10.4 False acceptance – better than 0.01%.

9.8.10.5 False rejection – better than 0.01%.

9.8.10.6 Recognition time – less than 1 sec.

9.8.10.7 Rugged plastic or metal case.

9.8.10.8 Indoor/Outdoor operation.

9.8.10.9 MTBF – better than 1,000,000 operations.
9.8.11 Controller
9.8.11.1 The controller is the computer interface that will be installed in the building to coordinate between the card readers and the system server/computer and will give local permissions for opening the required door.  The controller will include in its memory an updated list of all people authorized to enter and this list will be updated by the system server.  The controller will have an autonomous role and will allow regular operation even if the communication with the server falls or is interrupted.  The controller will be connected to the electrical network by a power plug and to the communication network by an RJ45 plug.

9.8.11.2 The controller will be able to identify 20,000 records of people authorized to enter.

9.8.11.3 The controller will be able to serve all the readers within the area in which it is installed.

9.8.11.4 The communication protocol between the controller and the system server will be TCP/IP.

9.8.11.5 The controller will be installed in close proximity to a communication cabinet/box located in the building.  The exact location for the installation of the building controller will be decided by the customer at the appropriate stage of installation planning.

9.8.11.6 The controllers will be installed within a metal box.

9.8.11.7 The controller will be fitted out in a humidity-proof sealed box suitable for indoors.

9.8.11.8 Minimum hardware requirements for the controller are:

9.8.11.8.1 The controller will include between 8 – 12 RS 232 input ports, 1 10 Base (BNC) and 1 10 Base T output ports (RJ45).

9.8.11.8.2 The controller will include at least 4 logical outputs of the ‘dry contact’ type which are required for the operation of the electric locks and local indicators for authorization/denial of entry and operation of the buzzer.

9.8.11.8.3 The controller should have at least 10Mb RAM.

9.8.11.8.4 The controller should have at least 512Kb of flash ROM.

9.8.11.8.5 The size of the controller memory which identifies the requests from the readers should be sufficient for 20,000 user names and 5,000 operations.  The controller memory must be backed up by a battery to provide at least 12 hours of operation.
[image: image2.emf]
Appendix A: IP cameras and CCTV standard
Information Security Guidelines

1. Laws and Regulations

1.1 The Vendor undertakes to comply with all the provisions of the Computers Law, Protection of Privacy Law and Database Law, and to comply with any future legislation that will apply to Customs and VAT receiving service from an external vendor. In addition, the Vendor undertakes to respect and implement any existing or future law relating to the management of protected/limited information, lawful management of databases containing individual data and maintenance of confidentiality regarding individual data and personal identification details.

2. Management of Databases

2.1 The Vendor undertakes to comply with the instructions in the field of information security in Customs and VAT in all matters pertaining to the management of information and services, which are the subject of the Agreement (Part C of the Protection of Privacy Regulations, Conditions of Holding and Maintaining Information).

3. Information Security Officer

3.1 The Vendor shall appoint one of the Company's employees to serve as an Information Security Officer, who shall be responsible on its behalf for the security of the information under the law, regulations and procedures to be transferred to it under this Agreement.

4. Reporting information security events

4.1 The Vendor must implement an information security event handling procedure. The Information Security Officer acting on behalf of the Vendor shall report to the Information Security Department in Customs and VAT authorities any detected information security event, which relates, whether directly or indirectly, to Customs and VAT.
5. Employee Reliability

5.1  The Vendor undertakes to carry out reliability tests and periodic assessments of sensitive position holders and employees, who will have access to information, software infrastructure and IT facilities.

5.2  An employee shall not be employed as a system user with an access to information or as a provider of support or technical services regarding IT and communications without performing reliability checks and without the approval of the Senior Department of Emergency Information and Cyber Security.
6. Building Entrance Control

6.1 The Vendor shall operate security and entrance control in buildings, in which systems and databases used by Customs and VAT are installed.

6.2  The Vendor shall maintain and control access to any area under its responsibility, from which access to infrastructure connected to the systems used by Customs and VAT is possible.

7. Information Provision

7.1 The Vendor shall not provide information from the Customs and VAT databases or information received by it in connection with the Agreement execution, as well as information on the security of the systems, which are the subject of the Agreement, to any entity or person, beyond the foregoing, without obtaining a written approval of an authorized party specified in the Agreement.

8. Audits

8.1 The Vendor undertakes to enable the Security/Customs and VAT Division representatives to carry out security audits during normal work hours at the Company's facilities, which are related to or have an influence on the security of the systems used by Customs and VAT.

8.2  Customs and VAT or authorized representatives on its behalf shall be entitled to perform security checks, immunity control, detection of security breaches and examination of the effectiveness of mechanisms used to secure the systems used by Customs and VAT.
9. Termination of Agreement

9.1  All the undertakings of the Vendor and its employees to maintain confidentiality of information during the term of agreement shall be in force even following the termination.

9.2  The Vendor shall not retain any materials or data provided to it by Customs and VAT representatives receiving the service or by any other party due to the Agreement.

9.3  Any means of IT and identification that belong to Customs and VAT shall be returned even if it is no longer in use.

9.4 Each memory platform containing personal data or a telephone list shall be returned to Customs and VAT.

Appendix B: Information & Cyber Security
1. General requirements

1.1 The vendor/winner/service provider, including the sub-vendors and all those involved in development, establishment or maintenance, shall comply with all information and cyber security requirements, whether the guidelines are specified in the Information Security Appendix or will be provided later, after the winner has been determined.

1.2 As part of the tender, the vendor will be required to design, build and maintain active/passive IT environments/communication networks, while these environments should support the processes required for the full operation of the Tax Authority – Customs Department Radiography System.

1.3 The vendor shall ensure that all information security requirements are implemented across all components, including off-the-shelf products to be purchased and implemented by the vendor as part of the project. In addition, the vendor should take care of all information security processes in systems under its responsibility and in connection with other systems in other environments.

1.4 At all stages of the project, the vendor is prohibited from connecting to the Tax Authority – Customs Department networks, including connection between the environment and the Internet.

1.5 All networks to be designed and built by the vendor should not be connected to the Internet in any way whatsoever.

1.6 At each stage of systems’ design and establishment, and for each service/component/infrastructure that will be integrated into the solution, a designated confirmation will be required in the field of information security at the Tax Authority – Customs Department.

1.7 The bidder shall specify all the aspects of cyber security of the proposed solution, at the data protection level, systems protection and IT infrastructure protection, as well as other components, regarding the following aspects in particular:
1.7.1  The topology, particularly the information security architecture (including “information about the information”, i.e. information, monitoring and control), including the following aspects: FW-check point, Fortinet, Palo Alto (one of the manufacturers in the list).
1.7.1.1  Confidentiality of information that meets the requirements of the law and privacy.

1.7.1.2 Information security when idle, processing and moving.

1.7.1.3 Identification mechanisms, strong identification.

1.7.1.4 Blocking using Device Control.

1.7.2 The bidder must describe the proposed topology components, hardware, software, information flow paths and hardening.

2. Requirements regarding vendor’s planning and implementation

2.1 Physical security and information security

2.1.1 Physical security aspects shall be defined based on the instructions of the Tax Authority – Customs Department Chief Security Officer, as specified in the Physical Security Appendix.

2.1.2 Personnel reliability: project personnel shall be classified in accordance with the instructions of the Chief Security Officer throughout the stages of the project. 

2.1.3 Release of information: it is hereby clarified that the use of visitors’ cell phone use should be restricted; in addition, it is prohibited to take out material, hard or soft, related to the activity of the radiography System across all its environments, off site/facility, including printing of information from various networks on the site or Radiography System output (radiography images).

2.2 Compliance with the requirements of the law, regulations and information security standards

2.2.1 The proposed solution must comply with the information security and other requirements specified in the latest version of the following laws, regulations, standards and specifications. It should be clarified that the vendor requirement relates only to infrastructures and systems under vendor’s responsibility and not to the customer’s systems, i.e. the local environment of the vendor (the entire IT infrastructure at the Authority’s service center), and the infrastructure to be established for implementation of interfaces to internal systems of the Tax Authority – Customs Department.

2.2.1.1 Provisions of any law relating to computerized systems, particularly the Computers Law, 5755-1995, Copyright Law, 5768-2007, and intellectual property.

2.2.1.2 Protection of Privacy Law, 5741-1981 (including the Protection of Privacy Regulations/Regulation 13).

2.2.1.3 Information Security Policy of the Tax Authority – Customs Department.

2.3 Verification, management of identities and permissions

2.3.1 The vendor will describe the identification mechanisms spanning all systems, users and interfaces that the solution supports and the way he will comply with the requirements.

2.3.2 The solution must support a strong identification mechanism for all project systems and infrastructures. It should be noted that for users’ access, the identification should be based on 2FA (Two factor authentication). Password length, complexity and validity should be determined by the customer in the project planning stages.

2.3.3 In networks under vendor’s responsibility, users will be centrally managed through an enterprise directory, such as Active Directory.

2.3.4 Wherever possible, the system should support the SSO of the user upon connecting to the management interfaces and the user.

2.3.5 It is prohibited to use Shared Credential in operating systems, applications, administrators, etc. Implementation should be carried out via procedures and controls.

2.3.6 The vendor will describe all roles in various systems and the extent of the existing permissions for each role in the environment. The entire solution should support Role-Base Access Control.

2.3.7 The vendor will describe the built-in permission management mechanisms in various systems in the solution, and interfacing with an external identity management system, such as Active Directory & LDAP.

2.3.8 The system should support a central permission mechanism in accordance with system requirements, which should support the following principles:

2.3.8.1 Minimal permission principle: in every system and in each system component, access should be allowed only to authorized and minimized entities as much as possible.

2.3.8.2 Restrict access to system resources: restrict users who access resources such as files, folders, registry keys, etc., and what they can do (reading, writing, creating, running and deleting).

2.3.8.3 Minimal permissions for the database user: upon accessing the database for data validation, retrieval and updating, it is necessary to ensure that the permissions are for Store Procedure only or as minimal as possible.

2.3.9 The solution should support provision of permissions for identification at the operating system level, communication components, databases and application based on AD (active directory) users/groups.

2.3.10 The vendor is required to lock connections as a result of temporary inactivity, and not to allow connection continuity until user’s identification and re-authorization. As part of connection locking, information displayed on the screen must be hidden prior to locking.

2.3.11 The vendor is required to restrict user login to the system after several failed login attempts by locking the option to log in for a specified period of time or until the lock is released by system administrator. The number of failed attempts to connect can be limited within the Group Policy and Domain Policy.

2.3.12 The vendor is required to limit the number of allowed simultaneous connections per single user as much as possible. The number of simultaneous connections can be limited within the Logon Remote Policy and Group Policy.

2.4  Network Security

2.4.1 The vendor is required to protect its services against service denial attacks and implement control via these tools:

2.4.1.1 The vendor must design and establish a firewall system to separate the server environment from the various users’ environment.

2.4.2 The media switches must be configured with a strong user name and password and should not be left with default settings. Management should be carried out via encrypted protocols, using a personal password that belongs to a specific technician and a dedicated segment to be configured for management purposes and enabled in the firewall.

2.4.3 It is required to implement mechanisms to prevent unauthorized physical connection to the network. The bidder is required to provide a solution via design, supply, implementation and operation of a network access control system (NAC), Clear Pass, Cisco, Portnox (one of the manufacturers).

2.5 Separation of passive networks infrastructure

2.5.1 The vendor is required to design and implement separate network cables/fibers/racks for different networks that are physically separated. For example, Tax Authority – Customs Department network infrastructures should never be connected to the radiography System network or other networks.

2.5.2 The vendor must carry out passive separation, including separate IT/communication rooms for each network.

2.5.3 Exceptions can be made with the written approval of the Information Security Department at the Tax Authority – Customs Department for communication racks that are not located in dedicated communication rooms. Confirmation regarding this matter, as well as confirmation of the implementation method, shall be obtained at the Information Security Department at the Tax Authority – Customs Department.

2.6 Terminals and servers security

2.6.1 The winning vendor will harden all systems provided and/or under its responsibility, such as Switches, Windows Servers, Databases, AV, Firewalls, etc. This hardening should be based on Best Practices used in the market and by various manufacturers.

2.6.2 The winning vendor will implement any requirement of the customer regarding the hardening of any system/infrastructure/product, provided that the hardening does not require the vendor to purchase any unplanned designated software/hardware proposed by it as part of responding to the tender.

2.6.3 The vendor is required to disable/remove all transmitting components, including BT, WIFI, NFC from system terminals and servers. In addition, it is necessary to disable/remove unused interfaces, such as camera, microphone, speaker, etc.

2.6.4 The bidder must implement security software against malware and viruses by using antivirus/antimalware products to be installed on all user stations and servers in the organization.

2.6.4.1 Identification between the system and media shall be based on serial number verification at the operating system level (device control).

2.6.4.2 Operating system and protection tools updates should be carried out via a designated external device to be approved at the serial number level in device control.

2.6.5 Input of information into the radiography system shall be carried out using a designated data screening solution (CDR - content disarm & reconstruction) that will be provided by the customer.

2.7 Updates and patch management

2.7.1 The winning vendor must ensure that operating system updates and information security updates are carried out on a regular basis (once every two weeks). Critical security updates in security systems should be installed immediately, once the update is released. In addition, in each version update, the operating system and various protection tools must be updated. 

2.8 Application security

2.8.1 The vendor must prove via the Company’s official approval that all the systems to be provided as part of the tender are developed under secure development standards acceptable in the market, such as SDLC.

2.8.2 The vendor must ensure that all products are fully hardened and implemented prior to operating the systems in production.

2.9 Logs monitoring, collection, management and analysis

2.9.1 The vendor is required to deliver logs collection, monitoring and analysis systems for project networks (radiography system, physical security network) to be connected to all components of the solution without exception:

2.9.1.1 Any action, particularly by the administrators, must be documented in a security record and sent to the monitoring computer.

2.9.1.2 System administrators, in accordance with their authorization, shall define the components, in which the activity will be documented in the log files and audit logs.

2.9.1.3 A capability will be required for logs’ transfer to the security monitoring computer in accordance with accepted standards, such as SYSLOG.

2.9.2 The bidder must describe all monitoring capabilities of the proposed solution, including communications, servers, security systems, information systems, databases, etc.

2.9.3 The system shall recognize deviation from normal behavior patterns (anomalies), such as multiple requests, irregular user actions, etc.

2.9.4 The bidder will specify and describe all logs registered in all the proposed solution’s systems, which can be integrated into the vendor’s security system to be implemented in the monitoring computer.

2.9.5 During the detailed design phase, the vendor will provide a detailed plan regarding the configuration of cyber monitoring and the proposed correlations to be implemented in cyber monitoring systems it will establish, for the purpose of monitoring required for investigations to detect and analyze suspicious activities. The plan should include alerts and screens tailored for research and full monitoring, in accordance with the requirements of the Information Security Department at the Tax Authority – Customs Department.

2.9.6 The system should maintain historical information on each activity for a parametric period to be determined by the customer for the purpose of peripheral monitoring, examinations and surveys of the customer and provision of legal response.

2.10 Code surveys, risk surveys and penetration tests

2.10.1 The customer shall be entitled to perform penetration tests and code surveys regarding all components of the solution both prior to introduction and launch of the system and as a condition for launching the version and upgrading the software, and every 18 months as of the previous survey/test, even if no change has been made in this period of time.

2.10.2 Any significant change in the technological solution to be implemented by the winning vendor will require a renewed risk assessment and penetration tests and code survey in accordance with the instructions of the Information Security Department at the Tax Authority – Customs Department.

2.10.3 The vendor should inform the client once all malfunctions are eliminated, if any, as a condition for obtaining approval for launching or upgrading the solution.

2.10.4 The winning vendor should enable, assist, provide information and support the representatives of the Information Security Department at the Tax Authority – Customs Department, or any other entity acting on its behalf, in carrying out any survey/test/audit upon customer’s demand.

2.11 Reports and escalation

2.11.1 The vendor shall appoint, in cooperation with the Information Security Department of the Tax Authority – Customs Department, an Information Security Officer, who shall serve as a single point of contact to the Information Security Department.

2.11.2 The vendor shall immediately report any event and/or suspicion of an event and/or technological event that disrupts the normal operation of the facility across all its systems.

2.11.3 For the avoidance of doubt, the vendor is responsible to handle any information security event immediately upon detection, until the threat is fully eliminated, including using all resources required.

2.11.4 Closing a cybersecurity event shall be possible upon the customer’s approval only, particularly upon the approval of a representative in the field of information security.

2.11.5 The vendor is aware that it is strictly prohibited to extract any records and/or files from the radiography system. Any material or record extraction requires the approval of the Information Security Department of the Tax Authority – Customs Department.

SOW Haifa port

Section 6-G_FCS 25.7.2019
6G-1
17/7/18
27
SOW Haifa port

Section 6-G FCS
6G-1
10.9.2019

